## SUMMARY (hidden)
Nepal Government
Ministry of Physical Planning and Work
Department of Water Supply and Sewerage
Drinking Water Quality Improvement Project
Summary of Cost
Project: …………………... Water Quality Improvement Project
Q = | 8.0 LPS
S.N. | Description of Works | No. | Quantity |  | Total Amount
(NRs.)
1 | Land Acquisition | 1 | Ropani | 100000 | 100000
2 | Site Development | 1 | job | 461020.8 | 461020.8
3 | Intake Maintenance | 1 | No. | …………. | …………….
4 | Plain Sedimentation Tank | 1 | No. | 2290087.16 | 2290087.16
5 | Horizontal Roughing Filter | 1 | No. | 3276895.27 | 3276895.27
6 | Slow Sand Filter | 1 | No. | 9727725.63 | 9727725.63
7 | Disinfection Chamber | 1 | No. | 23964.09 | 23964.09
8 | Sand Wash Platform | 1 | No. | 77097.77 | 77097.77
9 | Pipes and Fittings Procurement | 1 | job | 3775975.56 | 3775975.56
10 | Pipe Line Relaying and Jointing | 1 | job | 27334 | 27334
8 | Chlorine Dosing Unit with accessories and Fitting | 1 | No. | 70000 | 70000
11 | Compound Wall with Barbed Wire Fencing
| and Gate | 1 | job | 2969130 | 2969130
13 | Chaukidar Quarters | 1 | No. | 1204585.78 | 1204585.78
12 | Reservoir Maintenance | 1 | No. | 500000 | …………….
13 | Protection Works | 1 | job | 4256716.49 | 4256716.49
14 | Training and Orientation / Water Quality Campaigns | 1 | package | 94350 | 94350
| Sub Total |  |  |  | 28354882.55
| 2.5 % Contingencies |  |  |  | 708872.06
| Grand Total |  |  |  | 29063754.61

## Salient feature (hidden)
Salient Features ( Schemewise ) of Project
District: Kathmandu
1 | Name of Project | Sankhu Drinking Water Supply Project
2 | Name of District |  | Kathmandu | Kathmandu
3 | Name of Municipality |  | Shankharapur | Shankharapur
4 | Wards Covered |  | 3 | 4
5 | Number of Schemes |  | 1 | 1
Sn | Parameters | Unit | Fedi (Sc-1) | Damai Kholsi (Sc-2)
A. | General Parameter
1 | Households(Survey year:2017) | No. | 133 | 134
2 | Population(Survey year:2017) | No. | 857 | 763
3 | Households(Base year:2019) | No. | 136.5074 | 137.5338
4 | Population(Base year:2019) | No. | 898 | 788
5 | Households(Design year:2039) | No. | 177.0935 | 178.425
6 | Population(Design year:2039) | No. | 1155 | 1023
1 | Design Period | Yrs. | 20 | 20
2 | Annual growth rate | % | 3.5 | 3.5
B. | Source Information
1 | Source Name |  | Fedi | Damai Kholsi
2 | Source Type & Number | Type/No. | Spring | Spring
3 | Tapped Discharge source - | Lps | 20 | 12
4 | Approximate Distance from Project Site | km | 1 | 1.02
4 | Water Quality of Source |  | Fair | Fair
C. | Water provision & Demand
1 | Provision for Domestic use | lpcd | 69300 | 61380
3 | Provision for Institutional use | lpcd | 4320 | 2000
4 | Provision for Live Stock | Yes/No | No | No
5 | Total Water Demand (Design Year) | Lpd | 73620 | 63380
C. | Project Components
1 | Actual Length of Transmission Main | km | 0.11 | 0
2 | Actual Length of Distribution Pipe Line | km | 0 | 2.175
3 | Institutional connections | No. | 2 | 1
4 | Number of Private Connection Provided | No. | 138.5074 | 138.5338
5 | Reservoir Number/ Capacity | m³/no | 20,4 | 20,2
6 | Total Number of CC, DC, IC, VC & AVC | No. | 12 | 6
7 | Crossing | No. | No | No
8 | Institutional latrine | No. | No | No
E. | Project Cost Data
1 | Total Estimated Cost(without physical & price adjustment contingencies | NRs. | 38849700.1654 | 20106828.16
2 | Average Per Capita Cost at Base Year | NRs. | 43262.4723 | 25516.2794
3 | Average Per Capita Cost at Design Year | NRs. | 33636.104 | 19654.7685
2 | Community Contribution Amount as per Estimate | NRs. | 3884970.0165 | 4011500.32
3 | Community Contribution as per % of Estimate | % | 10% | 10.5
4 | Number of WUSC Members/VMW | No.

## sum cost_All (hidden)
Summary of Cost ( With Schemewise Cost )
Name of Scheme: Sankhu Drinking Water Supply Project
Sn | Items | Unit | Fedi (Sc-1) |  |  | Damai Kholsi (Sc-2) |  |  | Total
|  |  | Unit Rate | Qty | Amount | Unit Rate | Qty | Amount | Qty | Amount
A | Community Education Awareness
Program
1 | Pre-construction Training | no | [6 empty] | 1 | 25000
2 | Appraisal & Comm. Preparation | no | [6 empty] | 1 | 14000
3 | VMWs Training | no | [6 empty] | 1 | 15000
4 | Pre-handover Training | no | [6 empty] | 1 | 15000
5 | Motivators/Volunteers Training | no | [6 empty] | 1 | 10000
| Total A | [8 empty] | 79000
B | Water Supply & Sanitation
B1 | Civil Works
1 | Detailed Survey & Design Work | % | 150000 | 0 | 0 | 150000 | 0 | 0 | 0 | 0
2 | Stream intake(without VC) | no | 1631664.65 | 1 | 1631664.65 | 254293.6293 | 1 | 254293.6293 | 2 | 1885958.2793
3 | Collection Chamber | no | 226732.014 | 1 | 226732.014 | 155943.49 | 1 | 155943.49 | 2 | 382675.504
4 | Plain Sedimentation Tank | no |  |  | Existing | 2290087.16 | 1 | 2290087.16 | 1 | 2290087.16
5 | Horizontal Roughing Filter | no |  |  | Existing | 3276895.27 | 1 | 3276895.27 | 1 | 3276895.27
6 | Slow Sand Filter | no |  |  | Existing | 9727725.63 | 1 | 9727725.63 | 1 | 9727725.63
7 | Disinfection Chamber | no |  |  | Existing | 23964.09 | 1 | 23964.09 | 1 | 23964.09
8 | Sand Wash Platform | no |  |  |  | 77097.77 | 1 | 77097.77 | 1 | 77097.77
9 | 400 cum Reservoir at Fedi and Damai Kholsi | no | 7521398.2562 | 1 | 7521398.2562 | 7521398.2562 | 1 | 7521398.2562 |  | 15042796.5123
9 | Pipes and Fittings Procurement | no | [6 empty] | 1 | 3775975.56
10 | Pipe Line Relaying and Jointing | no |  |  |  | 163192.62 | 1 | 163192.62 | 1 | 163192.62
12 | Chlorine Dosing Unit with accessories and Fitting | no
13 | Compound Wall with Barbed Wire Fencing and Gate | no |  |  |  | 2969130 | 1 | 2969130 | 1 | 2969130
14 | Retaining wall | no | 25361.13 | 100 | 2536113 | 25361.13 | 50 | 1268056.5 | 150 | 3804169.5
15 | PCC pitching in river | m |  | 50 | 231671.29 |  |  |  |  | 231671.29
15 | Chaukidar Quarters | no | 1204585.78 | 1 | 1204585.78 | 1204585.78 | 1 | 1204585.78 |  | 2409171.56
16 | WTP Maintenance including plaster in RVT | no | 500000 | 1 | 500000 |  |  |  | 1 | 500000
17 | Protection Works | no |  |  |  | 452546.99 | 1 | 452546.99 | 1 | 452546.99
18 | Private Connection (including institution) | no | 12407.5808 | 0 | 0 | 9723.79 | 139 | 1351606.81 | 139 | 1351606.81
18 | Distribution Chamber (Two chamber) | no | 111224.4988 | 1 | 111224.4988 | 79374.31 | 1 | 79374.31 | 2 | 190598.8088
19 | Air Valve Chamber at Junction | no | 19092.5286 | 4 | 76370.1145 | 12956.91 | 2 | 25913.82 | 6 | 102283.9345
20 | Washout Valve Chamber | no | 41591.2588 | 7 | 291138.8113 | 28436.44 | 3 | 85309.32 | 10 | 376448.1313
21 | Sectional Valve Chamber at Junction | no | 41591.2588 | 6 | 249547.5526 | 28436.44 | 1 | 28436.44 | 7 | 277983.9926
22 | BPC/IC | no | 58624.4113 | 1 | 58624.4113 | 43505.51 | 1 | 43505.51 | 2 | 102129.9213
23 | Roof Truss in existing | no | 2747456.5347 | 1 | 2747456.5347 | 2747456.5347 | 1 | 2747456.5347 | 2 | 5494913.0694
24 | Sump Well System |  | 2054351.3587 | 1 | 2054351.3587 |  |  |  | 1 | 2054351.3587
25 | Pipe Support for pipeline | no | 22164.7252 | 20 | 443294.5036 | 22164.7252 | 12 | 265976.7022 | 32 | 709271.2058
26 | Pipeline works ( E/W and jointing )
| i. Transmission | Km |  | 0.175 |  |  | 1.18 |  | 1.355 | 399326.4851
| ii. Distribution | Km |  | 2.87 |  |  | 3.2 |  | 6.07 | 5295880.5774
27 | Transportation of Pipes, Fittings & Tools from store to site) | % |  | 1 |  |  | 1 |  | 2 | 455262.2503
| Sub-Total (B1) |  |  |  | 19884172.7757 |  |  | 34012496.6323 |  | 63823114.2808
B2 | Materials & Equipments
1 | Pipes | km |  | 5.332 | 18965527.3898 |  | 3.97 |  | 9.302 | 18965527.3898
2 | Fittings | % | [6 empty] | 1 | 1119506.3341
3 | Tools & Plants | % | [6 empty] | 1 | 141602.108
| Sub-Total (B2) |  |  |  | 18965527.3898 |  |  | 2275899.64 |  | 20226635.8318
| Total B (B1+B2) |  |  |  | 38849700.1654 |  |  | 20027828.16 |  | 84049750.1126
| Total (A+B) |  |  |  | 38849700.1654 |  |  | 20106828.16 |  | 84128750.1126
C | Contingencies & Overhead
1 | Contingencies 2 % of (A+B) |  |  |  | 776994.0033 |  |  | 402136.5632 |  | 1682575.0023
2 | Sanitation Component 2 % of (A+B) |  |  |  | 776994.0033 |  |  | 402136.5632 |  | 1682575.0023
| Total C |  |  |  | 1553988.0066 |  |  | 804273.1264 |  | 3365150.0045
| Total Cost of Scheme (A+B+C) |  |  |  | 40403688.1721 |  |  | 20911101.2864 |  | 87493900.1171
| Add Physical Contingencies@10% |  |  |  | 4040368.8172 |  |  | 2091110.1286 |  | 8749390.0117
| Add Price Escalation@10% |  |  |  | 4040368.8172 |  |  | 2091110.1286 |  | 8749390.0117
| Total Cost of Project : |  |  |  | 48484425.8065 |  |  | 25093321.5437 |  | 104992680.1406

## COST_ALL (hidden)
Abstract of Cost
Component: Plain Sedimentation Tank
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Site Clearence | 1 | 84 | m2 | 137.54 | 11553.36
2 | Earth Work in Excavation in
| Foundation in Boulder Mixed Soil | 1 | 142.92 | m 3 | 1732.69 | 247636.05
3 | Earth Filling in Foundation | 1 | 30.13 | m 3 | 653.84 | 19700.2
4 | Stone Soling with sand packing on
| Base of Foundation, | 1 | 15.02 | m 3 | 10963.48 | 164671.47
5 | Laying of P.C.C. 1:3:6 on Base of
| Foundation | 1 | 7.8 | m 3 | 14330.41 | 111777.2
6 | Laying of One Layer Tarfelt Over
| Lean Concrete | 1 | 72.04 | m 2 | 702.36 | 50598.01
7 | P.C.C (1: 1.5:3) Works for R.C.C | 1 | 27.78 | m 3 | 16948.41 | 470826.83
8 | Centring and Shuttering Works for
| P.C.C. and R.C.C Works | 1 | 191.39 | m 2 | 1278.27 | 244648.1
9 | Reiforcement Works with Deformed
bars Bars Including supplying,
Cutting, Bending and Placing in
| Position | 1 | 5003.04 | kg | 123.56 | 618175.62
10 | Brick Masonry Work in 1:6
| Cement Sand mortar | 1 | 2.62 | m 2 | 18942.74 | 49629.98
11 | 12.5 mm Thick Cement Sand Plaster
in 1:3 Mortar with 2% Water Proof
| Compound | 1 | 171.55 | m 2 | 486.67 | 83488.24
12 | 20 mm Thick Cement Sand Plaster in
| 1:4 Mortar in Base Slab | 1 | 96 | m 2 | 609 | 58464
13 | 3 mm Thick Punning in 1: 1 Cement
| Sand Mortar | 1 | 7.8 | m 2 | 332.33 | 2592.17
14 | Two Coat of Enamel Paint of
Appropriate Colour on Exposed
| Surface of Tank | 1 | 68.89 | m 2 | 378.44 | 26070.73
15 | Installation of 4 inch dia. Pipe
Pieces and Fittings for Inlet, Outlet and
W/O Complete as per Drawing and
| Specification |  | lump sum |  |  | 2000
16 | Standard Manhole Cover (60cm dia)
including M.S. Angle of 1.5" in
Size including Fixing all Complete as
| per Drawing and Specification | 1 | 2 | No. | 6500 | 13000
17 | Site Development around the
| Sedimentation Unit | 1 | 30 | m | 3841.84 | 115255.2
|  |  | Total |  |  | 2290087.16
Component: Horizontal Roughing Filter
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Site Clearence | 1 | 81 | m2 | 137.54 | 11140.74
2 | Earth Work in Excavation in
| Foundation in Boulder Mixed Soil | 1 | 129.38 | m 3 | 1732.69 | 224175.43
3 | Earth Filling in Foundation in Boulder
| Mixed Soil | 1 | 9.54 | m 3 | 653.84 | 6237.63
4 | Stone Soling with sand packing on
| Base of Foundation | 1 | 16.87 | m 3 | 10963.48 | 184953.91
5 | Laying of P.C.C. 1:3:6 on Base of
| Foundation | 1 | 8.58 | m 3 | 14330.41 | 122954.92
6 | Laying of One Layer Tarfelt Over
| Lean Concrete | 1 | 89.3 | m 2 | 702.36 | 62720.75
7 | P.C.C (1: 1.5:3) Works for R.C.C | 1 | 36.44 | m 3 | 16948.41 | 617600.06
8 | Centring and Shuttering Works for
| P.C.C. and R.C.C Works | 1 | 252.93 | m 2 | 1278.27 | 323312.83
9 | Reiforcement Works with Deformed bars
Bars Including Supplying,Cutting,
| Bending and Placing in Position | 1 | 1935.66 | kg | 123.56 | 239170.15
10 | Brick Masonry Work in 1:4
| Cement Sand mortar | 1 | 1.22 | m 3 | 18942.74 | 23110.14
11 | 12.5 mm Thick Cement Sand Plaster in
1:3 Mortar with 2% Water Proof
| Compound | 1 | 271.17 | m 2 | 486.67 | 131970.3
12 | 20 mm Thick Cement Sand Plaster in
| 1:4 Mortar in | 1 | 67.2 | m 2 | 609 | 40924.8
13 | 3 mm Thick Punning in 1: 1 Cement
| Sand Mortar | 1 | 250.76 | m 2 | 332.33 | 83335.07
14 | Two Coat of Enamel Paint of
Appropriate Colour on Exposed
| Surface of Tank | 1 | 78.53 | m 2 | 378.44 | 29718.89
15 | Preparation and Placing of 40-20 mm
dia. Gravel Filter Media as per
| Specification | 1 | 21 | m 3 | 9150.1 | 192152.1
16 | Preparation and Placing of 20-10 mm
dia. Gravel Filter Media as per
| Specification | 1 | 31.5 | m 3 | 11397.72 | 359028.18
17 | Preparation and Placing of 04-10 mm
dia. Gravel Filter Media as per
| Specification | 1 | 31.5 | m 3 | 16323.34 | 514185.21
18 | Installation of 4 inch dia. Pipe
Pipe Pieces and Fittings for Inlet,
Outlet and W/O Complete including
| gates as per Drawing and Specification | 1 | 1 | Job | 5000 | 5000
19 | Standard Manhole Cover (60cm dia)
including M.S. Angle of 1.5" in
Size including Fixing all Complete as
| per Drawing and Specification | 1 | 2 | Nos. | 6500 | 13000
20 | Site Development around the HRF | 1 | 24 | m | 3841.84 | 92204.16
|  |  | Total |  |  | 3276895.27
Component: Slow Sand Filter
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Site Clearence | 1 | 196 | m2 | 137.54 | 26957.84
2 | Earth Work in Excavation in
| Foundation in Boulder Mixed Soil | 1 | 381.56 | m 3 | 1732.69 | 661125.2
3 | Earth Filling in Foundation | 1 | 31.97 | m 3 | 653.84 | 20903.26
4 | Stone Soling with sand packing on Base of Foundation | 1 | 40.1 | m 3 | 10963.48 | 439635.55
5 | Laying of P.C.C. 1:3:6 on Base of
| Foundation | 1 | 20.05 | m 3 | 14330.41 | 287324.72
6 | Laying of One Layer Tarfelt Over Lean
| Concrete | 1 | 191.37 | m 2 | 702.36 | 134410.63
7 | P.C.C (1: 1.5:3) Works for R.C.C | 1 | 92.69 | m 3 | 16948.41 | 1570948.12
8 | Centring and Shuttering Works for
| P.C.C. and R.C.C Works | 1 | 385.99 | m 2 | 1278.27 | 493399.44
9 | Reiforcement Works with Deformed
Bars Including Supplying,Cutting,
| Bending and Placing in Position | 1 | 9965.43 | kg | 123.56 | 1231328.53
10 | Brick Masonry Work in 1:4
| Cement Sand mortar | 1 | 6.1 | m 3 | 18942.74 | 115550.71
11 | 12.5 mm Thick Cement Sand Plaster in
1:3 Mortar with 2% Water Proof
| Compound | 1 | 398.91 | m 2 | 486.67 | 194137.53
12 | 20 mm Thick Cement Sand Plaster in
| 1:4 Mortar in Base Slab | 1 | 145.44 | m 2 | 609 | 88572.96
13 | 3 mm Thick Punning in 1: 1 Cement
| Sand Mortar | 1 | 364.7 | m 2 | 332.33 | 121200.75
14 | Smoothly Finished Brick Masonry
| Support in 1:4 Cement Sand Mortar | 1 | 5.47 | m 3 | 18942.74 | 103616.79
15 | HDPE Perforated Pipe of
| Manifold 140 mm dia.10 kg/cm2 | 1 | 24.48 | rm | 1171.78 | 28685.17
| Laterals 63 mm dia.10 kg/cm2 | 1 | 162.6 | rm | 242.55 | 39438.63
16 | Preparation and Placing of Gravel
| Filter Media 3 to 6 mm as per Spec. | 1 | 28.8 | m 3 | 16323.34 | 470112.19
17 | Preparation and Placing of Gravel
| Filter Media 6 to 20 rrim as per Spec. | 1 | 21.6 | m 3 | 11397.72 | 246190.75
Component: Slow Sand Filter
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
18 | Preparation and Placing of Gravel
| Filter Media 20 to 40 mm as per Spec. | 1 | 21.6 | m 3 | 9150.1 | 197642.16
19 | Preparation and Placing of Filter
| Sand as per Specification | 1 | 144 | m 3 | 20746.84 | 2987544.96
20 | Two Coat of Enamel Paint of appropriate
| Colour on Exposed Surface of Tank | 1 | 129.37 | m 2 | 378.44 | 48958.78
21 | Installation charges of 4 inch dia. Pipe
Pieces and Fittings for Inlet, Outlet
and W/O Complete as per Drawing
| and Specification | 1 |  | L. S. | 10000 | 10000
22 | Connection of laterals with manifold and
Installation charges of 140 mm dia.HDPE
| Pipe for Manifold | 1 |  | L. S. | 10000 | 10000
23 | Preparation of holes and Installation
charges of 63 mm dia.HDPE Pipe for
| Laterals | 1 |  | L. S. | 5000 | 5000
24 | Standard Manhole Cover (60cm dia)
including M.S. Angle of 1.5" in
Size including Fixing all Complete as
| per Drawing and Specification | 1 | 4 | L. S. | 6500 | 26000
25 | Site Development around the SSF | 1 | 44 | m | 3841.84 | 169040.96
|  |  |  | Total |  | 9727725.63
Component: Disinfection Chamber
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Site Clearence | 1 | 4 | m 2 | 137.54 | 550.16
2 | Earth Work in Excavation in
| Foundation in Boulder Mixed Soil | 1 | 0.9 | m 3 | 1732.69 | 1559.42
3 | Boulder Soling with Sand packing | 1 | 0.34 | m 3 | 10963.48 | 3727.58
4 | P.C.C (1: 2 : 4) on Base and top | 1 | 0.26 | m 3 | 15694.9 | 4080.67
5 | Brick Masonry Work in
| 1:4 Cement Sand mortar | 1 | 0.24 | m 3 | 18942.74 | 4546.26
6 | Supply of 500 litres capacity HDPE
tank with necessary fittings including
| pipes and feeding accessories | 1 | 1 | job | 6500 | 6500
7 | Installation of Pipe Pieces and
Fittings for Inlet, Outlet and W/O
Complete as per Drawing and
| Specification for 500 litres tank | 1 | 1 | job | 3000 | 3000
|  |  |  | Total |  | 23964.09
Component: Sand Wash Platform
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Site Clearence | 1 | 16 | m 2 | 137.54 | 2200.64
2 | Earth Work Excavation in Foundation
| in Boulder Mixed Soil | 1 | 5.6 | m 3 | 1732.69 | 9703.06
3 | Stone Soling in Base of Foundation | 1 | 3.2 | m 3 | 653.84 | 2092.29
4 | Laying of P.C.C. 1:3:6 on Base of
| Foundation | 1 | 1.6 | m 3 | 14330.41 | 22928.66
5 | M 15 P.C.C. (1:2:4) in Panel of
| 2.0 m x 1.0 m | 1 | 1.6 | m 2 | 15694.9 | 25111.84
6 | 20 mm Thick Cement Sand Plaster in
| 1:4 Mortar in Base Slab | 1 | 16 | m 2 | 609 | 9744
7 | 3 mm Thick Punning in 1: 1 Cement
| Sand Mortar | 1 | 16 | m 3 | 332.33 | 5317.28
|  |  |  | Total |  | 77097.77
Component: Site Development Work
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Site Clearence | 1 | 16 | m 2 | 137.54 | 2200.64
2 | Earth Work Excavation in Boulder
| and Gravel Mixed Soil | 1 | 4.8 | m 3 | 1732.69 | 8316.91
3 | Earth Filling with Compaction
| Layer with Sprinkling of Water | 1 | 1 | m 3 | 653.84 | 653.84
4 | Dry Stone Soling with sand | 1 | 1.5 | m 3 | 10963.48 | 16445.22
5 | P.C.C. (1:3:6) | 1 | 0.4 | m 3 | 14330.41 | 5732.16
6 | Brick Masonry Work with 1:6
| Cement Mortar | 1 | 0 | m 3 | 18532.78 | 0
7 | 12.5 mm Thick Cement Sand Plaster
| in 1:4 mortar | 1 | 10.6 | m 2 | 478.27 | 5069.66
|  |  |  | Total |  | 38418.43
Rate per meter | [5 empty] | 3841.84
Per running meter cost of site development work = |  |  | 120 | 3841.84 |  | 461020.8
Component: Barbed Wire Fencing with Compound Wall
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
BARBED WIRE FENCING
1 | Site Clearance |  | L.S. |  |  | 1000
2 | Earthwork in excavation pillars in BMS
| walls | 1 | 4.33 | m³ | 1732.69 | 7502.55
3 | Dry stone packing | 1 | 0.73 | m³ | 10963.48 | 8003.34
4 | PCC (1:2:4) for anchor blocks | 1 | 0.98 | m³ | 15694.9 | 15381
5 | Stone masonry (1:6) cement mortar Pillars
| walls | 1 | 4.66 | m³ | 14084.92 | 65635.73
6 | Barbed wire fencing (16+1: one more lengths of barbed
| wire to be anchored on entrance gate). | 1 | 250.58 | m | 1426.8 | 357527.54
7 | 6 mm ø mild steel rod for hooks, | 1 | 5.15 | kg | 123.56 | 636.33
650 mm long each
8 | M.S. 40 x 40 x 6 angle bar, 2.5 m long | 1 | 156.8 | kg | 123.56 | 19374.21
|  |  |  | Total |  | 475060.7
Per running meter cost = | [5 empty] | 19794.2
Total Fencing Work |  | 1 | 150 | m | 19794.2 | 2969130
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
ENTRANCE GATE
1 | Site Clearance |  | L.S. |  |  | 200
2 | Earthwork in excavation in foundation | 2 | 0.43 | m³ | 1732.69 | 1490.11
3 | Boulder masonry in (1:6) cement mortar
| for Pillar | 1 | 1.08 | m³ | 14084.92 | 15211.71
4 | Cement pointing in (1:6) for | 1 | 5.63 | m² | 361.27 | 2033.95
5 | 25 x 25 x 3 m Size Mild Steel angle
frames gate with Iron Grill shutter
(3.5 x 1.5 m size) all complete including
| fixing no. | 1 | 1 | No. | 15000 | 15000
6 | Enamel Painting for Gate | 1 | 1.43 | m² | 378.44 | 541.17
|  |  |  | Total |  | 34476.94
Total Fencing Work with Gate | [5 empty] | 3003606.94
Component: Chaukidar Quarter
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Site Clearance | 1 | 33.6 | m 2 | 137.54 | 4621.34
2 | Earthwork in excavation for foundation
| in hard soil | 1 | 22.09 | m 3 | 1362.18 | 30090.56
3 | Earth filling in hard soil | 1 | 1.39 | m 3 | 686.54 | 954.29
4 | Boulder soling with sand | 1 | 5.67 | m 3 | 10963.48 | 62162.93
5 | Laying of 500 gauge polythene sheet | 1 | 24.99 | m 2 | 185.96 | 4647.14
6 | Stone masonry in 1:6 cement sand mortar | 1 | 7.74 | m 3 | 14084.92 | 109017.28
7 | P.C.C. (1:2:4) | 1 | 5.31 | m 3 | 15694.9 | 83339.92
8 | Brick masonry work in 1:6 cement
| sand mortar for drain | 1 | 17.46 | m 3 | 18532.78 | 323582.34
9 | Centering & Shuttering work for PCC | 1 | 43.58 | m 2 | 1278.27 | 55707.01
10 | Reinforcement with deformend bars | 1 | 380.3 | kg | 123.56 | 46989.87
11 | Salwood work for Chaukhats | 1 | 0.18 | m 3 | 326279.6 | 58730.33
12 | 38 mm thick salwood panelled
| shutters | 1 | 2.89 | m 2 | 17634.79 | 50964.54
13 | 38 mm thick Sal wood glazed shutters | 1 | 2.85 | m 2 | 10386.54 | 29601.64
14 | 3 mm thick 1:1 cement sand punning
| on floor and skirting for | 1 | 40.76 | m 2 | 332.33 | 13545.77
15 | Cement plaster 12.5 mm thick
| 1:4 C/S mortar | 1 | 154.23 | m 2 | 478.27 | 73763.58
16 | 2 coats of white washing | 1 | 119.13 | m 2 | 200.01 | 23827.19
17 | Readymade enamel paint two coats
| with one coat of primer | 1 | 14.14 | m 2 | 378.44 | 5351.14
18 | Electrification and Sanitary work |  | L.S |  |  | 20000
|  |  |  | Total |  | 996896.87
POUR FLUSH LATRINE
1 | Site Clearance | 1 | 6 | m² | 137.54 | 825.24
2 | Earthwork in excavation in hard soil in foundation for | 1 | 6.0074 | m³ | 1362.18 | 8183.2
3 | Stone soling with sand | 1 | 0.34061 | m³ | 10963.48 | 3734.24
4 | Dry stone masonry | 1 | 1.2622 | m³ | 6783.38 | 8562.32
5 | Stone masonry in mud mortar | 1 | 6.767 | m³ | 7213.55 | 48814.27
6 | Stone masonry in 1:4 cement mortar | 1 | 3.517 | m³ | 14865.17 | 52280.8
7 | Squatting Pan | 1 | 1 | No. | 1800 | 1800
8 | PCC in slab cover for pits 1:2:4 | 1 | 0.51091 | m³ | 15694.9 | 8018.69
9 | MS reinforcement | 1 | 60.1921 | kgs | 123.56 | 7437.33
10 | 20 mm thick cement plaster (1:3) | 1 | 3.1 | m² | 624.02 | 1934.46
11 | Cement Pointing work in 1:3 mortar | 1 | 7.125 | m² | 361.27 | 2574.05
12 | Salwood work for Chaukhats | 1 | 0.10603 | m³ | 326279.6 | 34593.79
13 | 38 mm thick door shutter with wooden
| frame and GI plain sheet | 1 | 0.9639 | m² | 17634.79 | 16998.17
14 | Outlet Pipe (6 m long, 110 mm 6 Kg/cm2
| ø HDP pipe) | 1 | 12 | m | 464.2 | 5570.4
15 | Mosquito Screen | 1 | 0.195 | m² | 250 | 48.75
16 | 26 gauge CGI sheet roofing | 1 | 6 | m² | 1052.2 | 6313.2
|  |  |  | Total |  | 207688.91
|  |  |  | Total |  | 1204585.78
Component: Retaining wall on Treatment Plant site (For 10 m Length)
On Treatment Plant and existing Intake site
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Site Clearance | 1 | 20 | m 2 | 137.54 | 2750.8
2 | Earthwork in excavation for foundation
| in boulder mixed soil | 1 | 6 | m 3 | 1732.69 | 10396.14
3 | Earth filling in boulder mixed soil | 1 | 4.8 | m 3 | 653.84 | 3138.43
4 | Dry boulder soling | 1 | 1.8 | m 3 | 5141.87 | 9255.37
5 | Stone masonry in 1:6 cement sand mortar | 1 | 15.5 | m 3 | 14084.92 | 218316.26
6 | Cement pointing 1:3 on external | 1 | 27 | m 2 | 361.27 | 9754.29
|  |  |  | Total |  | 253611.29
Per running meter cost = | [5 empty] | 25361.13
Total Retaining Work |  | 1 | 150 | m | 25361.13 | 3804169.5
Component: Catch Drain at Treatment Plant site (For 10 m Length)
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | E/W in excavation in Boulder mixed soil | 1 | 4 | m 3 | 5141.87 | 20567.48
2 | Dry boulder soling | 1 | 1.5 | m 3 | 5141.87 | 7712.81
3 | P.C.C. 1:2:4 | 1 | 0.23 | m 3 | 15694.9 | 3609.83
4 | R.R. masonary in 1: 6 Cement sand mortar | 1 | 2.45 | m 3 | 14084.92 | 34508.05
5 | Cement pointing with 1:3 C/S mortar | 1 | 18.6 | m 2 | 361.27 | 6719.62
|  |  |  | Total |  | 73117.79
Per running meter cost = | [5 empty] | 7311.78
Total cost of Catch Drain Work |  | 1 | 25 | m | 7311.78 | 182794.5
Component: Access road Construction up to Treatment Plant site (For 10 m Length)
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | E/W in excavation in Boulder mixed soil | 1 | 18 | m 3 | 1732.69 | 31188.42
|  |  |  | Total |  | 31188.42
Per running meter cost = | [5 empty] | 3118.84
Total cost of Access Road Construction Work |  | 1 | 50 | m | 3118.84 | 155942
Component: Pipe Laying and Relaying Work
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | E/W in excavation in BMS | 1 | 54 | m3 | 1732.69 | 93565.26
2 | Earthwork refilling in BMS | 1 | 54 | m3 | 653.84 | 35307.36
3 | Laying and Jointing of 75 mm |  |  |  |  | 0
| dia. HDPE pipe of 10 kg/cm2 | 1 | 100 | r m | 343.2 | 34320
|  |  |  | Total |  | 163192.62
Component: Gabion Work
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Gabion preparation, mesh forming etc.
| (3 m x1 m x 1 m) | 1 | 6 | no. | 7605.525 | 45633.15
2 | Filling of Gabion box with stone | 1 | 18 | m3 | 3787.63 | 68177.34
|  |  |  | Total |  | 113810.49
Component: Protection Work
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Retaining wall |  |  |  |  | 3804169.5
2 | Catch Drain |  |  |  |  | 182794.5
3 | Access road Construction |  |  |  |  | 155942
4 | Gabion Work |  |  |  |  | 113810.49
Total Protection Work | [5 empty] | 4256716.49
Component : Pipe & Fittings
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
A | Intake Hilechaur
1 | 4" G.I./HDPE Flange |  | 8 | no. | 2406 | 19248
2 | 4" G.I.Nipple 6" long |  | 12 | no. | 917 | 11004
4 | 4" GI Gate Valve |  | 4 | no. | 23238 | 92952
5 | 4" G.I. Elbow |  | 8 | no. | 2159 | 17272
6 | 110 mm HDPE elbow |  | 6 | no. | 695 | 4170
7 | 110 mm HDPE Tee |  | 6 | no. | 695 | 4170
8 | 4" G.I. /G.I.Flange |  | 4 | no. | 6948 | 27792
B | Intake Fedi
1 | 4" G.I./HDPE Flange |  | 4 | no. | 2406 | 9624
2 | 4" G.I.Nipple 6" long |  | 8 | no. | 917 | 7336
4 | 4" GI Gate Valve |  | 4 | no. | 23238 | 92952
5 | 4" G.I. Elbow |  | 8 | no. | 2159 | 17272
6 | 110 mm HDPE elbow |  | 5 | no. | 695 | 3475
7 | 110 mm HDPE Tee |  | 2 | no. | 695 | 1390
8 | 4" G.I. /G.I.Flange |  | 4 | no. | 6948 | 27792
C | Sedimentation Unit
1 | 4" G.I./HDPE Flange |  | 6 | no. | 2406 | 14436
2 | 4" G.I.Nipple 6" long |  | 12 | no. | 917 | 11004
4 | 4" GI Gate Valve |  | 5 | no. | 23238 | 116190
5 | 4" G.I. Elbow |  | 6 | no. | 2159 | 12954
6 | 110 mm HDPE elbow |  | 5 | no. | 695 | 3475
7 | 110 mm HDPE Tee |  | 2 | no. | 695 | 1390
8 | 4" G.I. /G.I.Flange |  | 4 | no. | 6948 | 27792
D | Horizontal Roughing filter
1 | 4" G.I./HDPE Flange |  | 4 | no. | 2406 | 9624
2 | 4" G.I.Nipple 6" long |  | 10 | no. | 917 | 9170
3 | 4" GI Gate Valve |  | 4 | no. | 23238 | 92952
4 | 4" G.I. Elbow |  | 4 | no. | 2159 | 8636
7 | 110 mm HDPE Tee |  | 3 | no. | 695 | 2085
5 | 4" G.I. /G.I.Flange |  | 4 | no. | 6948 | 27792
E | Slow Sand Filter
1 | 4" G.I./HDPE Flange |  | 4 | no. | 2406 | 9624
2 | 4" G.I.Nipple 6" long |  | 16 | no. | 917 | 14672
3 | 4" GI Gate Valve |  | 8 | no. | 23238 | 185904
4 | 4" G.I. Elbow |  | 12 | no. | 2159 | 25908
5 | 4" G.I. /G.I.Flange |  | 14 | no. | 6948 | 97272
6 | 4" G.I.cross Tee |  | 2 | no. | 3363.1 | 6726.2
F | Reservoir
1 | 6" G.I./HDPE Flange |  | 4 | no. | 3505 | 14020
2 | 6" G.I.Nipple 6" long |  | 16 | no. | 3007.5 | 48120
3 | 6" GI Gate Valve |  | 8 | no. | 34857 | 278856
4 | 6" G.I. Elbow |  | 12 | no. | 6430 | 77160
5 | 6" G.I. /G.I.Flange |  | 14 | no. | 10422 | 145908
6 | 6" G.I.cross Tee |  | 2 | no. | 6726.2 | 13452.4
F | Fittings for disinfection chamber
| and other works |  | L.S. |  |  | 10000
|  |  |  | Sub Total |  | 1601571.6
| Add transportation @ 5 % |  |  |  |  | 80078.58
|  |  |  | Sub Total |  | 1681650.18
| Add Contractors Overhead |  |  |  |  | 252247.53
|  |  |  | Sub Total |  | 1933897.71
| Add VAT 13 % |  |  |  |  | 251406.7
|  |  |  | Total |  | 2185304.41
G | Pipe requirement for the treatment units
1 | 4" G.I. Medium Class |  | 50 | rm | 23238 | 1161900
2 | 110 mm PE100 10 kg/cm2 (Inlet, Outlet, Washout) |  | 50 | rm | 726.83 | 36341.5
H | Pipe and fitting requirement for Improvement of line
1 | 75 mm dia. PE100 10 kg/cm2 |  | 100 | rm | 1424 | 142400
|  |  |  | Sub Total |  | 1340641.5
| Add transportation @ 5 % |  |  |  |  | 67032.08
|  |  |  | Sub Total |  | 1407673.58
| Add VAT 13 % |  |  |  |  | 182997.57
|  |  |  | Total |  | 1590671.15
|  |  |  | Total |  | 3775975.56
Component: Training Components
S.N. | Description of Works | No. | Quantity | Unit | Unit Rate | Total Amount
1 | Awareness Programme (7 Days)
| a. Training Expert | 1 | 10 | days | 1500 | 15000
| b. Training Assistant | 1 | 10 | days | 800 | 8000
| c. Audio-Video (Hire Charge & Production) | 1 | 2 | no | 2000 | 4000
| d. Poster Distribution | 1 | 1500 | no | 10 | 15000
| e. Mass Meeting (Tea and Snacks, paper etc.) | 1 | 50 | no | 25 | 1250
| f. Transportation | 1 | 2 | persons | 1000 | 2000
| g. Miscellaneous | 1 |  | L.S. |  | 4000
| Sub-Total: |  |  |  |  | 49250
2 | Water Quality, On Site Sanitation & Waste Disposal
Institutional Strengthening,
Operation and Maintenance
Training (7 Days) 20 persons
| a. Training Expert | 1 | 10 | days | 1500 | 15000
| b. Training Assistant | 1 | 7 | days | 800 | 5600
| c. Sr. Mason | 1 | 5 | days | 800 | 4000
| d. Allowance and Snacks for Trainees | 1 | 7 | days | 500 | 3500
| e. File, Pen & Stationaries | 1 | 20 | pack | 50 | 1000
| f. Pour Flush Latrine construction | 1 | 1 | no | 3000 | 3000
| g. Transportation | 1 | 2 | persons | 1000 | 2000
h.Training Manual Preparation
| Production | 1 | 20 | set | 300 | 6000
| i. Miscellaneous | 1 |  | L.S. |  | 5000
| Sub-Total: |  |  |  |  | 45100
| Total |  |  | Total |  | 94350

## Cost RVT-400 (hidden)
COST ESTIMATE OF CIRCULAR RCC RESERVOIR 400 Cu m
Type of Building :- Circular RCC Reservoir 400 cu m | [5 empty] | Civil Works
S.No. | Description | Unit | Quantity | Rate | Amount | Remarks
1 | Site Clearance | m2 | 153.938 | 137.54 | 21172.638
0
2 | Earthwork in excavation in foundation | m3 | 207.8164 | 1732.69 | 360081.3185
0
3 | Stone soling | m3 | 30.3494 | 5141.87 | 156052.4423
[5 empty] | 0 |  |  | 1810.191 | 1.578 | 2856.4814
4 | Plain Cement Concrete P.C.C. (M10) in 1:3:6 | m3 | 22.762 | 14330.41 | 326189.0342 |  |  | 2278.72 | 0.888 | 2023.5034
[5 empty] | 0 |  |  | 3731.636 | 0.62 | 2313.6143
5 | Cement Concrete work for R.C.C (1:1.5:3) (M20) | m3 | 202.7593 | 16948.41 | 3436447.8595 |  |  | 2218.933 | 0.395 | 876.4785
[5 empty] | 0 |  |  |  |  | 8070.0776
6 | Reinforcement Bar for RCC | Kg | 12562 | 123.56 | 1552160.72
[5 empty] | 0 |  |  |  |  | 807.0078
7 | Erecting, centering and shuttering of formwork for RCC | m2 | 524.2241 | 1278.27 | 670099.8857 |  |  |  |  | 8877.0854
0
8 | 12.5 mm thick outside cement plaster in 1:4 C/M | m2 | 320.406 | 478.27 | 153240.5951
0
9 | 20 mm thick cement plaster inside tank 1:3 C/M | m2 | 270.3969 | 624.02 | 168733.0609 |  |  | 3179.6555 | -0.084 | -267.0911
[5 empty] | 0 |  |  | 3447.5697 | -0.4657 | -1605.5332
10 | 12.5 mm thick Cement Sand plaster in 1:4 C/M in Ceiling | m2 | 111.5944 | 609 | 67960.9881 |  |  | 3715.4839 | -0.8474 | -3148.5011
[5 empty] | 0 |  |  | 3983.3981 | -1.2291 | -4895.9946
11-a | Providing Crystalline Water Proof Treatment | m2 | 381.9913 | 893.5609 | 341332.4668 |  |  |  |  | -9917.1199
0
11-b | 3 mm thick Cement Punning | m2 | 381.9913 | 332.33 | 126947.1612 |  |  | 3879.2092 | -1.0807 | -4192.1106
[5 empty] | 0 |  |  | 3983.3981 | -1.2291 | -4895.9946
12 | Earthwork in backfilling | m3 | 11.3537 | 653.84 | 7423.5136 |  |  | 4087.587 | -1.3775 | -5630.81
[5 empty] | 0 |  |  | 4191.7758 | -1.526 | -6396.5567
13 | 25 mm thick Plain G.l. Sheet of 16 SWG as a water-stop supplying and fixing | m | 39.2699 | 1052.2 | 41319.7974 |  |  | 4295.9647 | -1.6744 | -21115.4719
[5 empty] | 0 |  |  | 4400.1535 | -1.8229
14 | 32mm día. Gl pipe railings and staircase | m | 48 | 755.9741 | 36286.755 |  |  | 4504.3424 | -1.9713 | -2111.5472
0
15 | 2 coat enamel paint in railing & inspection ladders on top of primer | m2 | 48 | 378.44 | 18165.12
16 | Ventilations of Wooden Frame With Chicken Wire Mesh & Mosquito Mesh | Set | 4 | 8000 | 32000
16 | Ventilations of Wooden Frame With Chicken Wire Mesh & Mosquito Mesh | Set | 4 | 6.45 | 25.8
0
17 | Manhole Cover | Set | 2 | 2879.55 | 5759.1
0
| Total |  |  |  | 7521398.2562 |  |  | 5040469.2735
|  |  |  | 1 | 4.047 | 0.5 | 4.547
|  |  |  | 2 | 4.675 | 0.5 | 5.175
|  |  |  | 3 | 5.304 | 0.5 | 5.804
|  |  |  | 4 | 5.932 | 0.5 | 6.432
|  |  |  | 5 | 6.56 | 0.5 | 7.06
|  |  |  | 6 | 7.187 | 0.5 | 7.687
|  |  |  | 7 | 7.814 | 0.5 | 8.314
|  |  |  | 8 | 8.44 | 0.5 | 8.94
|  |  |  | 9 | 9.065 | 0.5 | 9.565
|  |  |  | 10 | 9.69 | 0.5 | 10.19
|  |  |  | 11 | 10.314 | 0.5 | 10.814
|  |  |  | 12 | 10.938 | 0.5 | 11.438
|  |  |  | 13 | 11.561 | 0.5 | 12.061
|  |  |  | 14 | 12.182 | 0.5 | 12.682
|  |  |  | 15 | 12.803 | 0.5 | 13.303
|  |  |  | 16 | 13.423 | 0.5 | 13.923
|  |  |  | 17 | 14.042 | 0.5 | 14.542
|  |  |  | 18 | 14.66 | 0.5 | 15.16
|  |  |  | 19 | 15.277 | 0.5 | 15.777
|  |  |  | 20 | 15.893 | 0.5 | 16.393
|  |  |  | 21 | 16.508 | 0.5 | 17.008
|  |  |  | 22 | 17.121 | 0.5 | 17.621
|  |  |  | 23 | 17.733 | 0.5 | 18.233
|  |  |  | 24 | 18.344 | 0.5 | 18.844
|  |  |  | 25 | 18.954 | 0.5 | 19.454
|  |  |  | 26 | 19.562 | 0.5 | 20.062
|  |  |  | 27 | 20.169 | 0.5 | 20.669
|  |  |  | 28 | 20.774 | 0.5 | 21.274
|  |  |  | 29 | 21.378 | 0.5 | 21.878
|  |  |  | 30 | 21.98 | 0.5 | 22.48
|  |  |  | 31 | 22.581 | 0.5 | 23.081
|  |  |  | 32 | 23.18 | 0.5 | 23.68
|  |  |  | 33 | 23.777 | 0.5 | 24.277
|  |  |  | 34 | 24.372 | 0.5 | 24.872
|  |  |  | 35 | 24.966 | 0.5 | 25.466
|  |  |  | 36 | 25.558 | 0.5 | 26.058
|  |  |  | 37 | 26.148 | 0.5 | 26.648
|  |  |  | 38 | 26.736 | 0.5 | 27.236 |  | 72 | 5.514 | 397.008
|  |  |  | 39 | 27.323 | 0.5 | 27.823 |  | 66 | 4.5 | 297
|  |  |  | 40 | 27.907 | 0.5 | 28.407 |  |  |  | 694.008
|  |  |  | 41 | 28.489 | 0.5 | 28.989
|  |  |  | 42 | 29.069 | 0.5 | 29.569
|  |  |  | 43 | 29.647 | 0.5 | 30.147
|  |  |  | 44 | 30.223 | 0.5 | 30.723
|  |  |  | 45 | 30.797 | 0.5 | 31.297
|  |  |  | 46 | 31.368 | 0.5 | 31.868
|  |  |  | 47 | 31.937 | 0.5 | 32.437 |  |  |  | 1891.061
|  |  |  | 48 | 32.504 | 0.5 | 33.004
|  |  |  | 49 | 33.068 | 0.5 | 33.568
|  |  |  | 50 | 33.63 | 0.5 | 34.13
|  |  |  | 51 | 34.19 | 0.5 | 34.69
|  |  |  | 52 | 34.747 | 0.5 | 35.247
|  |  |  | 53 | 35.301 | 0.5 | 35.801
|  |  |  | 54 | 35.853 | 0.5 | 36.353
|  |  |  | 55 | 36.403 | 0.5 | 36.903
|  |  |  | 56 | 36.949 | 0.5 | 37.449
1197.053
3.927
0.5
4.427
[9 empty] | 3.79 | 2 | 7.58
[9 empty] | 4.42 | 2 | 8.84
20.6

## Sump well (hidden)
QUANTITY ESTIMATES
SUMP WELL FOR PUMPS IN GROUND RESERVOIR
S.No. | Description of Works | No. | Length (m) | Breadth (m) | Height (m) | Quantity | Rate | Amount
a | E/W in Excavation | 1 | 6.1 | 4.9 | 4.75 | 141.98 | 1732.69 | 246007.3262
b | Back Filling | 1 | 35% of Total Earth Work |  |  | 49.69 | 653.84 | 32489.3096
c | Stone Soling | 1 | 4.1 | 2.9 | 0.15 | 1.78 | 5141.87 | 9152.5286
d | M10 Cement Concrete Work for PCC | 1 | 4.1 | 2.9 | 0.1 | 1.19 | 14330.41 | 17053.1879
e | M20 Cement Concrete Work for PCC
| Bottom Slab | 1 | 4.1 | 2.9 | 0.4 | 4.76
| Long Wall | 2 | 3.4 | 0.35 | 5.1 | 12.14
| Short Wall | 2 | 1.5 | 0.35 | 5.1 | 5.36
| Roof Slab | 1 | 3.4 | 2.2 | 0.1 | 0.75
[5 empty] | Total | 23.01 | 16948.41 | 389982.9141
f | Formwork
| Foundation | 1 | 14 |  | 0.5 | 7
| Outer Side of Wall | 1 | 11.2 |  | 5.2 | 58.24
| Inner Side of Wall | 1 | 8.4 |  | 5.1 | 42.84
| Bottom Face of Slab | 1 | 2.7 |  | 1.5 | 4.05
[5 empty] | Total | 112.13 | 1278.27 | 143332.4151
g | Reinforcement
| 12 Dia. Bar in Base Slab in Longer Dir. | 38 | 5.3 | Unit Wt. | 0.899 | 181.06
| 12 Dia. Bar in Base Slab in Short Dir. | 52 | 4.1 | Unit Wt. | 0.899 | 191.67
| 16 Dia. Vertical Wall (Long) | 116 | 6.78 | Unit Wt. | 1.598 | 1256.8
| 16 Dia. Vertical Wall (Short) | 44 | 6.78 | Unit Wt. | 1.598 | 476.72
| 12 Dia. Horizontal Bar | 31 | 22.4 | Unit Wt. | 0.899 | 624.27
| 17 Dia. Bar in Base Slab in Longer Dir. | 20 | 3.7 | Unit Wt. | 0.4 | 29.6
| 8 Dia. Main Bar in Roof Slab | 14 | 2.5 | Unit Wt. | 0.4 | 14
| 8 Dia. Mainor Bar in Roof Slab | 34 | 1.9 | Unit Wt. | 0.4 | 25.84
| 8 Extra Bar in Roof Slab | 70 | 1.7 | Unit Wt. | 0.899 | 106.98
| 21 Dia. Chair Bar | 15% |  |  |  | 436.04
| Extra for Lapping, Chiar, etc. |  |  |  | Total | 3343 | 123.56 | 413061.08
h | Plaster (1:4) 12.5 and Punning
| Wall of Tank |  | Same as Inner form Work |  |  | 42.84
| Base of Tank | 1 | 2.7 | 1.5 |  | 4.05
[5 empty] | Total | 46.89 | 332.33 | 15582.9537
i | Plaster (1:4) 12.5 in Ceiling | 1 | 2.7 | 1.5 |  | 4.05 | 478.27 | 1936.9935
j | Providing Crystalline Cater Proof Treatment |  |  |  |  | 48.89 | 5000 | 244450
k | Mild Steel Iron Step | 54 |  |  |  | 54 | 225 | 12150
l | 600 X 600 Manhole Cover (Cash Iron) | 3 |  |  |  | 3 | 2879.55 | 8638.65
m | 18 SWG Water Stopper (with 15% for Lapping) | 3 | 11.2 |  |  | 39 | 526 | 20514
n | Pump Set and all accessories | 1 |  |  |  | 1 | 500000 | 500000
2054351.3587

## Abstract_TRUSS (hidden)
Abstract of Cost of Truss and Roofing
S.No. | Items Of works | Unit | Quantity | Unit rate | Amount | Remarks
1 | Clearing the site from trees, logs, bushes, weeds, grass, debris & rubbish of any nature to make the site suitable for construction work and clearing the site from construction materials and equipment after completion of the work as per instruction of the engineer. | Job | 1 | 20000 | 20000
2 | Earthwork in excavation in foundation in hard with a lead of 10 m. i> Upto depth 4M | cum | 90 | 1362.18 | 122596.2
3 | Providing and backfilling the earth in the trenches in layers not exceeding more than 225 mm with watering and ramming for the proper compaction as per the instruction and specification all complete. | cum | 27 | 544.87 | 14711.49
4 | Providing and laying first class chimney made brick soling on flat as per the instruction of the Engineer | sqm | 36 | 18942.74 | 681938.64
5 | Providing and laying of 75mm thick PCC (1:3:6) in foundation with a size of aggregate not exceeding 38 mm all complete as per the specification and instruction of the engineer | sqm | 2.7 | 14330.41 | 38692.107
6 | Supplying, mixing, placing, compacting and cure concrete PCC (1:1.5:3) for lintel as per drawing, specification and instruction of Engineer | cum | 4.5 | 16948.41 | 76267.845
7 | Brickwork in walls and foundation in cement sand mortar (1:4) with 1st class chimney bricks in perfect lines and levels with necessary scaffolding including wetting the brick, properly packing the joint with cement mortar and curing the works all complete | cum | 58.5 | 18942.74 | 1108150.29
8 | Providing and fitting of roof truss with black iron pipe including all necessary joints and accessories as per drawing and instruction, all complete. | Kgs | 546.3133 | 123.56 | 67502.4667
9 | Roofing with 0.5 mm thick corrugated coloured GI Sheet with necessary 8mm nut bolts, J-hooks, bitumin washers as per drawing and instruction, all complete. | Sft | 485.76 | 1052.2 | 511116.672
10 | Providing and fixing gutter of 0.5mm coloured plain sheet 150 mm width and 450 mm depth with 40*3 mm iron braket, nutbolt, washer, all complete | Rft | 36.8 | 1052.2 | 38720.96
11 | Providing and fixing ridge of 0.5mm coloured plain sheet , nutbolt, washer, all complete | Rft | 18.4 | 965.21 | 17759.864
17 | providing 10 SWG 3"X3" Chain mesh Fecing on all faces of the truss structure with metal door and proper locking system along with required support system | job | 1 | 50000 | 50000
|  |  |  | Total | 2747456.5347

## Pipe Support (hidden)
Detailed Quantity Estimate
Name of Scheme: Sankhu Drinking Water Supply Project
Component: Pipe Suppor Pillars
2 | 2m
| Earthwork Excavation | cu.m | 1 | 0.6 | 0.6 | 0.5 | 0.18 | 1732.69 | 311.8842
| Filling of trenches, | cu.m | 2 | 0.6 | 0.1 | 0.15 | 0.018 | 653.84 | 11.7691
|  |  | 2 | 0.4 | 0.1 | 0.15 | 0.012 | 653.84 | 7.8461
| Stone soling | cu.m | 1 | 0.6 | 0.6 | 0.2 | 0.072 | 5141.87 | 370.2146
| PCC 1:3:6 | cu.m | 1 | 0.6 | 0.6 | 0.15 | 0.054 | 14330.41 | 773.8421
| RRM in CM 1:4 | cu.m | 1 | 0.4 | 0.4 | 1 | 0.16 | 14865.17 | 2378.4272
| PCC 1:2:4 | cu.m | 1 | 0.4 | 0.4 | 0.1 | 0.016 | 15694.9 | 251.1184
4105.1018
2 | 2m
| Earthwork Excavation | cu.m | 1 | 1 | 1 | 0.8 | 0.8 | 1732.69 | 1386.152
| Filling of trenches, | cu.m | 2 | 1 | 0.1 | 0.45 | 0.09 | 653.84 | 58.8456
|  | cu.m | 2 | 0.8 | 0.1 | 0.45 | 0.072 | 653.84 | 47.0765
| Stone soling | cu.m | 1 | 1 | 1 | 0.2 | 0.2 | 5141.87 | 1028.374
| PCC 1:3:6 | cu.m | 1 | 1 | 1 | 0.15 | 0.15 | 14330.41 | 2149.5615
| RRM in CM 1:4 | cu.m | 1 | 0.8 | 0.8 | 1 | 0.64 | 14865.17 | 9513.7088
|  | cu.m | 1 | 0.4 | 0.4 | 1 | 0.16 | 14865.17 | 2378.4272
| PCC 1:2:4 | cu.m | 1 | 0.4 | 0.4 | 0.1 | 0.016 | 15694.9 | 251.1184
16813.264
3 | 3m
| Earthwork Excavation | cu.m | 1 | 1 | 1 | 0.8 | 0.8 | 1732.69 | 1386.152
| Filling of trenches, | cu.m | 2 | 1 | 0.1 | 0.45 | 0.09 | 653.84 | 58.8456
|  | cu.m | 2 | 0.8 | 0.1 | 0.45 | 0.072 | 653.84 | 47.0765
| Stone soling | cu.m | 1 | 1 | 1 | 0.2 | 0.2 | 5141.87 | 1028.374
| PCC 1:3:6 | cu.m | 1 | 1 | 1 | 0.15 | 0.15 | 14330.41 | 2149.5615
| RRM in CM 1:4 | cu.m | 1 | 0.8 | 0.8 | 1 | 0.64 | 14865.17 | 9513.7088
|  | cu.m | 1 | 0.6 | 0.6 | 1 | 0.36 | 14865.17 | 5351.4612
|  | cu.m | 1 | 0.4 | 0.4 | 1 | 0.16 | 14865.17 | 2378.4272
| PCC 1:2:4 | cu.m | 1 | 0.4 | 0.4 | 0.1 | 0.016 | 15694.9 | 251.1184
22164.7252
SN | >3m
1 | Earthwork Excavation | cu.m | 1 | 1.2 | 1.2 | 0.9 | 1.296 | 1732.69 | 2245.5662
2 | Filling of trenches, | cu.m | 2 | 1.2 | 0.4 | 0.4 | 0.384 | 653.84 | 251.0746
3 |  | cu.m | 2 | 0.4 | 0.4 | 0.4 | 0.128 | 653.84 | 83.6915
4 | Stone soling | cu.m | 1 | 1.2 | 1.2 | 0.2 | 0.288 | 5141.87 | 1480.8586
5 | RCC 1:2:4 | cu.m | 1 | 1.2 | 1.2 | 0.3 | 0.432 | 15694.9 | 6780.1968
|  | cu.m | 1 | 0.4 | 0.4 | 4 | 0.64 | 15694.9 | 10044.736
6 | TMT bars | kg | 16 | 1.2 | - | - | 19.2
|  | kg | 4 | 5 | - | - | 20
39.2
| 12mmØ | [5 empty] | 34.888 | 123.56 | 4310.7613
|  | kg | 20 | 1.6 |  |  | 32
| 8mmØ | [5 empty] | 12.64 | 123.56 | 1561.7984
7 | Shuttering | sq.m | 4 | 1.2 | - | 0.3 | 1.44 | 1278.27 | 1840.7088
|  |  | 4 | 0.4 | - | 4 | 6.4 | 1278.27 | 8180.928
[8 empty] | Total | 36780.3202
Component: Thrust Block
90°
| Description | Unit | No. | L | B | H | Qty | Rate
1 | Excavation | cu.m | 1 | 1 | 1 | 1.2 | 1.2 | 1732.69 | 140.244
2 | PCC 1:2:4, 40mm agg | cu.m | 1 | 1 | 1 | 1 | 1 | 15694.9 | 4263.96
3 | Shuttering | sq.m | 4 | 1 | - | 1 | 4 | 1278.27 | 1091.08
5495.284

## Cost_In_1 (hidden)
ABSTRACT OF COST
TYPE OF WORK : Intake Construction-Fedi
S.no. | Description of works | Unit | Quantity | Rate | Amount | Remarks
1 | Site Clearance | sqm | 170.4 | 137.54 | 23436.82 |  |  | 160920.01
2 | Earthwork Excavation in River Bed | Cum | 32.23 | 3269.22 | 105366.96
3 | Stone Soling | Cum | 6.93 | 5141.87 | 35633.16 |  | 35633.16 | #REF!
4 | P.C.C Works
4.1 | PCC M10 | Cum | 3.46 | 14330.41 | 49583.22 |  | 49583.22 | 49583.22
4.2 | RCC works M20 | cum | 24.95 | 16948.41 | 422862.83
5 | Form Works | sqm | 125.78 | 1278.27 | 160780.8 |  | #REF! | 160780.8
6 | Reinforcement | kg | 3965.553 | 123.56 | 489983.73 |  | #REF!
7 | 20 to 25mm thick screeding (1:4) on floors | sqm | 5.25 | 439.2689 | 2306.16
8 | Cement punning | sqm | 61.15 | 220.9771 | 13512.75
9 | 12.5 mm thick cement plaster on concrete surface with 1:3 cement sand mortar | sqm | 79.09 | 351.5055 | 27800.57 |  |  | 27800.57 | 2016 | 2073
10 | Gabion Works | [7 empty] | #REF! | 2060
| Launching Apron | [5 empty] | #REF!
| 2mx1mx0.3m | Cum | 44.52 | 6073.622 | 270397.65
12 | 600dia. Manhole Cover | No. | 2 | 15000 | 30000
13 | Supplying and laying Pipes Fittings
| 75∅ Tee | No. |  | 352 | 0
| 75∅ Elbow | No. |  | 313.5 | 0
| 75∅ Pipe Piece | No. |  | 452.18 | 0
| 65∅ Gate Valve | No. |  | 11221.096 | 0
| 65∅ Union | No. |  | 1046.2785 | 0
| 65∅ Nipple | No. |  | 443.2785 | 0
| 65/75 GI/PE Flanged set | No. |  | 1656.2785 | 0
| 75∅ PE Stainer | No. |  | 520.007 | 0
1631664.65
TYPE OF WORK : Pitching works in river
S.no. | Description of works | Unit | Quantity | Rate | Amount | Remarks
1 | Earthwork Excavation in River Bed | Cum | 134 | 414.575 | 55553.05
2 | Back filling | Cum | 30 | 296.125 | 8883.75
3 | Masonary Works
3.1 | Stone Soling | Cum | 16.8 | 4565 | 76692
3.2 | Stone Masonary(1:6) | Cum | 0 | 8027 | 0
4 | P.C.C Works
4.1 | M10 | Cum | 8.45 | 10715.0876 | 90542.49
4.2 | M15 | Cum | 0 | 12897.0127 | 0
5 | Form Works | sqm | 0 | 764.3315 | 0 |  |  |  |  | 10.8
6 | 12.5mm thick c/s plaster (1:3) in wall (both sides) and 100mm below GL | sqm | 0 | 351.5055 | 0 |  |  |  | 1.0972
7 | Fencing by galvanised chain link of 10SWG with 50mm bore MS pipe (@2m c/c), 25x25x4 mm MS angle & 100 mm long 3x20mm MS strip | sqm | 0 | 2250.18 | 0
8 | Gabions Works
| 2x1x1 | Cum | 0 | 2605.6285 | 0
|  |  |  | Total | 231671.29

## Qnty_ALL (hidden)
Detailed Quantity Estimate
Component: Plain Sedimentation Tank
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
1 | Site Clearence | 1 | 14 | 6 |  | 84 | m2
2 | Earth Work in Excavation in Boulder Mixed Soil
| Levelling work | 1 | 13.52 | 5.52 | 0.3 | 22.39
Foundation in Boulder Mixed Soil
| PS | 1 | 13.52 | 5.52 | 1.48 | 110.45
| Inlet VC | 1 | 1.83 | 1.86 | 1.48 | 5.04
| Outlet VC | 1 | 1.83 | 1.86 | 1.48 | 5.04
|  |  |  | Total |  | 142.92 | m3
3 | Earth Filling in Foundation
| Long wall | 2 | 13.52 | 0.6 | 1.48 | 24.01
| short wall | 2 | 4.32 | 0.6 | 1.48 | 7.67
| Inlet VC | 1 | 1.83 | 0.2 | 1.48 | 0.54
| Outlet VC | 1 | 1.83 | 0.2 | 1.48 | 0.54
|  |  |  | Sub Total |  | 32.76 | m3
Deduct
| Long wall | 2 | 13.52 | 0.15 | 0.48 | 1.95
| short wall | 2 | 4.32 | 0.15 | 0.48 | 0.62
| Inlet VC | 1 | 1.83 | 0.05 | 0.35 | 0.03
| Outlet VC | 1 | 1.83 | 0.05 | 0.35 | 0.03
|  |  |  | Total |  | 30.13 | m3
4 | Stone Soling with sand packing on
| Base of Foundation, PS | 1 | 13.22 | 5.22 | 0.2 | 13.8
| Inlet VC | 1 | 1.73 | 1.76 | 0.2 | 0.61
| Outlet VC | 1 | 1.73 | 1.76 | 0.2 | 0.61
|  |  |  | Total |  | 15.02 | m3
5 | Laying of P.C.C. 1:3:6 on Base of
| Foundation PS | 1 | 13.8 | 5.22 | 0.1 | 7.2
| Inlet VC | 1 | 1.73 | 1.76 | 0.1 | 0.3
| Outlet VC | 1 | 1.73 | 1.76 | 0.1 | 0.3
|  |  |  | Total |  | 7.8 | m3
6 | Laying of One Layer Tarfelt Over
| Lean Concrete PS | 1 | 13.8 | 5.22 |  | 72.04
|  |  |  | Total |  | 72.04 | m3
7 | P.C.C (1: 1.5:3) Works for R.C.C
SSF
| Base Slab | 1 | 13.22 | 5.22 | 0.18 | 12.42
| Long Wall | 2 | 12.32 | 0.16 | 1 | 3.94
| Long Wall | 2 | 12.32 | 0.18 | 1.4 | 6.21
| Short Wall | 2 | 4 | 0.16 | 1 | 1.28
| Short Wall | 2 | 4 | 0.18 | 1.4 | 2.02
| Channel base | 2 | 4.16 | 0.35 | 0.075 | 0.22
| height | 2 | 4.16 | 0.15 | 0.075 | 0.09
| Scum through collector base | 1 | 4.16 | 0.35 | 0.075 | 0.11
| height | 1 | 4.16 | 0.15 | 0.075 | 0.05
| Baffle | 1 | 4 | 0.075 | 1.2 | 0.36
Component: Plain Sedimentation Tank
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
| Baffle slab | 1 | 2 | 0.4 | 0.075 | 0.06
| Inlet VC | 1 | 1.73 | 1.76 | 0.1 | 0.3
| Outlet VC | 1 | 1.73 | 1.76 | 0.1 | 0.3
| Slab cover of Inlet VC | 1 | 1.66 | 1.46 | 0.1 | 0.24
| Slab cover of Outlet VC | 1 | 1.66 | 1.46 | 0.1 | 0.24
|  |  |  | Sub Total |  | 27.84 | m3
| Deduct manhole opening | 2 | 0.2826 |  | 0.1 | 0.06
|  |  |  | Total |  | 27.78 | m3
8 | Centring and Shuttering Works for
P.C.C. and R.C.C Works, PST
| Base Slab Long wall | 2 | 13.22 |  | 0.28 | 7.4
| Short Wall | 2 |  | 5.22 | 0.28 | 2.92
| Outer part of Long Wall | 2 | 12.32 |  | 2.4 | 59.14
| Inner part of Long Wall | 2 | 12 |  | 2.4 | 57.6
| Outer part of Short Wall | 2 | 4.32 |  | 2.4 | 20.74
| Inner part of Short Wall | 4 | 4 |  | 2.4 | 38.4
| Channel | 2 | 4.16 | 0.35 | 0.375 | 1.09
| Scum collector | 1 | 4.16 | 0.35 | 0.375 | 0.55
| Slab cover of Inlet VC | 1 | 1.2 | 1 |  | 1.2
| Slab cover of Outlet VC | 1 | 1.2 | 1 |  | 1.2
| sides Inlet VC | 2 | 4.32 | 0.1 |  | 0.86
| sides outlet VC | 2 | 4.32 | 0.1 |  | 0.86
| Baffle bottom | 1 | 4 | 0.075 |  | 0.3
| Baffle wall | 2 | 4 |  | 1.2 | 9.6
| Baffle slab | 1 | 2 | 0.4 |  | 0.8
| sides | 1 | 3.2 |  | 0.075 | 0.24
|  |  |  | Sub Total |  | 191.96
| Deduct manhole opening | 2 | 0.2826 |  |  | 0.57
|  |  |  | Total |  | 191.39 | m2
9 | Reiforcement Works with Deformed
bars Including supplying, Cutting,
Bending and Placing in Position
Base Slab
| Main bar 12 mm dia at 175mm c/c Hor top | 77 | 6.42 | 0.88171 | kg/m | 435.87
| Dist bar 10 mm dia at 200mm c/c Hor top | 28 | 14.22 | 0.6123 | kg/m | 243.79
| Main bar 12 mm dia at 175 mm c/c Hor bot | 77 | 6.42 | 0.88171 | kg/m | 435.87
| Dist bar 10 mm dia at 200 mm c/c Hor bot | 28 | 14.22 | 0.6123 | kg/m | 243.79
Haunch Bar
| Haunch bar 12 mm dia at 200mm c/c diag | 135 | 1.2 | 0.88171 | kg/m | 142.84
| Haunch bar 12 mm dia at 200mm c/c diag | 55 | 1.2 | 0.88171 | kg/m | 58.19
[6 empty] | 1560.35 | kg
Long Walls
| Main bar inner 12 mm dia 150mm c/c verIF | 167 | 3.18 | 0.88171 | kg/m | 468.24
| Dist bar 10 mm dia at 300 mm c/c Hor IF | 18 | 13.32 | 0.6123 | kg/m | 146.81
| Main bar outer 12 mm dia200mm c/c verOF | 126 | 3.18 | 0.88171 | kg/m | 353.28
| Dist bar 10 mm dia at 300 mm c/c Hor OF | 18 | 13.32 | 0.6123 | kg/m | 146.81
[6 empty] | 1115.14 | kg
Component: Plain Sedimentation Tank
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
Short Wall
| Main bar inner 12 mm dia200 mm c/c Hor IF | 26 | 4.92 | 0.88171 | kg/m | 112.79
| Dist bar 10 mm dia 300 mm c/c ver IF | 31 | 32.58 | 0.6123 | kg/m | 618.41
| Main bar outer 12mm dia 200mm c/c HorOF | 26 | 4.92 | 0.88171 | kg/m | 112.79
| Dist bar 10 mm dia at 300 mm c/c Hor OF | 31 | 32.58 | 0.6123 | kg/m | 618.41
[6 empty] | 1462.4 | kg
| Main bar both face up to 1m ht 12mm dia 200mm c/c ver | 341 | 1.78 | 0.88171 | kg/m | 535.18
Channel
| Main bar 10 mm @ 150 mm c/c | 29 | 1 | 0.6123 | kg/m | 17.76
| Distribution bar 10 mm @ 100 mm c/c | 14 | 4.16 | 0.6123 | kg/m | 35.66
| Scum collector | 29 | 1 | 0.6123 | kg/m | 17.76
|  | 14 | 4.16 | 0.6123 | kg/m | 35.66
| Baffle bottom | 25 | 0.75 | 0.6123 | kg/m | 11.48
| Baffle wall | 25 | 1 | 0.6123 | kg/m | 15.31
133.63
Slab of Valve Chamber
| Inlet VC Long side | 9 | 1.63 | 0.6123 | kg/m | 8.98
| Short side | 9 | 1.66 | 0.6123 | kg/m | 9.15
| Outlet VC one number Long side | 9 | 1.63 | 0.6123 | kg/m | 8.98
| Short side | 9 | 1.66 | 0.6123 | kg/m | 9.15
36.26
| Corner bars 12 mm dia @ 200 mm c/c | 52 | 3.504 | 0.88171 | kg/m | 160.65
|  |  |  | Sub Total |  | 5003.61 | kg
| Deduct manhole | 2 | 0.2826 |  |  | 0.57
| Net Reinforcement |  |  | Total |  | 5003.04 | kg
10 | Brick Masonry Work in 1:6 Cement Sand
mortar
| Inlet VC Long Wall | 2 | 1.43 | 0.23 | 1.48 | 0.97
| Short wall | 1 | 1 | 0.23 | 1.48 | 0.34
| Outlet VC Long Wall | 2 | 1.43 | 0.23 | 1.48 | 0.97
| Short wall | 1 | 1 | 0.23 | 1.48 | 0.34
|  |  |  | Total |  | 2.62
11 | 12.5 mm Thick Cement Sand Plaster
in 1:3 Mortar with 2% Water Proof
Compound PS
| Outer part of Outer Long Wall | 2 | 12.32 |  | 1.6 | 39.42
| Inner part of Outer Long Wall | 2 | 12 |  | 2.4 | 57.6
| Outer part of Short Wall | 2 | 4.48 |  | 1.6 | 14.34
| Inner part of Short Wall | 2 | 4 |  | 2.4 | 19.2
Component: Plain Sedimentation Tank
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
Top
| Long wall | 2 | 12.32 | 0.16 |  | 3.94
| short wall | 2 | 4 | 0.16 |  | 1.28
| Channel | 2 | 4.16 | 0.625 |  | 5.2
|  | 2 | 4.16 | 0.45 |  | 3.74
| Scum collector | 1 | 4.16 | 0.625 |  | 2.6
|  | 1 | 4.16 | 0.45 |  | 1.87
Valve chambers
| Outlet Outer part of Long Wall | 2 | 1.43 |  | 0.5 | 1.43
| Inner part of Long Wall | 2 | 1.2 |  | 1.48 | 3.55
| Outer part of Short Wall | 2 | 1.46 |  | 0.3 | 0.88
| Inner part of Short Wall | 2 | 1 |  | 1.48 | 2.96
| Inlet Outer part of Long Wall | 2 | 1.66 |  | 0.5 | 1.66
| Inner part of Long Wall | 2 | 1.2 |  | 1.48 | 3.55
| Outer part of Short Wall | 2 | 1.46 |  | 0.3 | 0.88
| Inner part of Short Wall | 2 | 1 |  | 1.48 | 2.96
Top
| Long wall | 4 | 1.43 | 0.16 |  | 0.92
| short wall | 4 | 1 | 0.16 |  | 0.64
Slabs
| Slab cover of Inlet VC | 1 | 1.2 | 1.46 |  | 1.75
| Slab cover of Outlet VC | 1 | 1.2 | 1.46 |  | 1.75
172.12
| Deduct manhole | 2 | 0.2826 |  |  | 0.57
|  |  |  | Total |  | 171.55 | m2
12 | 20 mm Thick Cement Sand Plaster in
1:4 Mortar in Base Slab
| SSF | 2 | 12 | 4 |  | 96
|  |  |  | Total |  | 96 | m2
13 | 3 mm Thick Punning in 1: 1 Cement
| Sand Mortar | inner plastered surfaces of SSF and CWC |  |  |  | 172.8 | m2
| Channel | 1 | 4.16 | 0.575 |  | 2.39
| Scum collector | 1 | 4.16 | 1.3 |  | 5.41
|  |  |  | Total |  | 7.8 | m2
14 | Two Coat of Enamel Paint of
| Appropriate Colour on Exposed | Outer plastered surfaces of SSF and CWC
| Surface of Tank |  |  |  |  | 68.89 | m2
15 | Installation of 5 inch dia. Pipe
Pieces and Fittings for Inlet, Outlet and W/O Complete as per Drawing
| and Specification | lumpsum |  |  |  | L.S.
16 | Standard Manhole Cover (60cm dia)
including M.S. Angle of 1.5" in
Size including Fixing all Complete as
| per Drawing and Specification | 2 |  |  |  | 2 | Nos.
Component: Roughing Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
1 | Site Clearence | 1 | 9 | 9 |  | 81 | m2
2 | Earth Work in Excavation in
| Levelling work | 1 | 10.88 | 8.74 | 0.3 | 28.53
| Foundation in Boulder Mixed Soil | 1 | 10.88 | 8.74 | 0.98 | 93.19
| Inlet valve chamber | 1 | 1.83 | 1.86 | 0.75 | 2.55
| Outlet valve cmaber | 2 | 1.83 | 1.86 | 0.75 | 5.11
|  |  |  | Total |  | 129.38 | m3
3 | Earth Filling in Foundation in Boulder
| Mixed Soil , long wall | 2 | 10.88 | 0.6 | 0.75 | 9.79
| Short wall | 2 | 7.54 | 0.6 | 0.75 | 6.79
| Inlet valve chamber , -long wall | 2 | 1.83 | 0.2 | 0.75 | 0.55
| short wall | 1 | 1.46 | 0.2 | 0.75 | 0.22
| Outlet valve chamber, -long wall | 2 | 1.83 | 0.2 | 0.75 | 0.55
| short wall | 1 | 1.46 | 0.2 | 0.75 | 0.22
|  |  |  | Sub Total |  | 18.12 | m3
| Deduct Long wall | 2 | 10.88 | 0.45 | 0.48 | 4.7
| short wall | 2 | 7.54 | 0.45 | 0.48 | 3.26
| Inlet valve chamber -long wall | 2 | 1.83 | 0.15 | 0.35 | 0.19
| short wall | 1 | 1.46 | 0.15 | 0.35 | 0.08
| Outlet valve chamber -long wall | 2 | 1.83 | 0.15 | 0.35 | 0.19
| short wall | 1 | 1.46 | 0.15 | 0.75 | 0.16
|  |  |  | Sub Total |  | 8.58
|  |  |  | Total |  | 9.54 | m3
4 | Stone Soling with sand packing on
| Base of Foundation , HRF | 1 | 10.58 | 7.54 | 0.2 | 15.95
| Inlet VC | 1 | 1.73 | 1.76 | 0.15 | 0.46
| Outlet VC | 1 | 1.73 | 1.76 | 0.15 | 0.46
|  |  |  | Total |  | 16.87 | m3
5 | Laying of P.C.C. 1:3:6 on Base of
| Foundation HRF | 1 | 10.58 | 7.54 | 0.1 | 7.98
| Inlet VC | 1 | 1.73 | 1.76 | 0.1 | 0.3
| Outlet VC | 1 | 1.73 | 1.76 | 0.1 | 0.3
|  |  |  | Total |  | 8.58 | m3
6 | Laying of One Layer Tarfelt Over
| Lean Concrete HRF | 1 | 10.58 | 8.44 |  | 89.3 | m2
7 | P.C.C (1: 1.5:3) Works for R.C.C
| HRF Base Slab | 1 | 10.58 | 7.54 | 0.18 | 14.36
| Outer Long Wall | 2 | 9.68 | 0.18 | 1.6 | 5.58
| Central Long Wall | 1 | 9.68 | 0.18 | 1.6 | 2.79
| Short Wall Outer | 2 | 7.54 | 0.18 | 1.6 | 4.34
| Slotted Wall | 8 | 3.5 | 0.18 | 1.6 | 8.06
| Inlet & outlet channel-base | 2 | 7.72 | 0.3 | 0.075 | 0.35
| Channel walls | 2 | 7.72 | 0.075 | 0.15 | 0.17
| Inlet VC | 1 | 1.73 | 1.76 | 0.1 | 0.3
Component: Roughing Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
| Outlet VC | 1 | 1.73 | 1.76 | 0.1 | 0.3
| Inlet Valve Chamber cover Slab | 1 | 1.43 | 1.46 | 0.1 | 0.21
| Outlet Valve Chambercover Slab | 1 | 1.43 | 1.46 | 0.1 | 0.21
|  |  |  | Sub Total |  | 36.67 | m3
| Deduction Inlet weir | 1 | 9.68 | 0.18 | 0.1 | 0.17
| manhole opening | 2 | 0.2826 |  | 0.1 | 0.06
|  |  |  | Sub Total |  | 0.23
| Net PCC Required |  |  | Total |  | 36.44 | m3
8 | Centring and Shuttering Works for
P.C.C. and R.C.C Works
| HRF Base Slab Long wall | 2 | 10.58 |  | 0.28 | 5.92
| short wall | 2 | 7.54 |  | 0.28 | 4.22
| Long Wall Outer | 2 | 9.68 |  | 1.6 | 30.98
| Short Wall Outer | 2 | 7.54 |  | 1.6 | 24.13
| Short Wall inner | 20 | 3.5 |  | 1.6 | 112
| Long Wall Inner | 4 | 2 |  | 1.6 | 12.8
| Long Wall Inner | 8 | 3 |  | 1.6 | 38.4
| Long Wall Inner | 8 | 0.8 |  | 1.6 | 10.24
Inlet and Outlet Channel
| outer base | 2 | 7.54 | 0.3 |  | 4.52
| wall | 2 | 7.54 |  | 0.375 | 5.66
| Slab cover of Inlet VC | 1 | 1.2 | 1 |  | 1.2
| Slab cover of Outlet VC | 1 | 1.2 | 1 |  | 1.2
| sides Inlet VC | 2 | 4.32 | 0.1 |  | 0.86
| sides outlet VC | 2 | 4.32 | 0.1 |  | 0.86
|  |  |  | Sub Total |  | 252.99 | m2
| Deduction manhole opening | 2 | 0.2826 |  | 0.1 | 0.06
|  |  |  | Total |  | 252.93 | m2
9 | Reiforcement Works with Deformed bars
Bars Including Supplying,Cutting,
Bending and Placing in Position
Base Slab
| Main bar 12 mm dia at 200 mm c/c Horizontally on top face | 54 | 9.64 | 0.88171 | kg/m | 458.98
| Dist bar 12 mm dia at 200 mm c/c Horizontally on top face | 44 | 11.78 | 0.88171 | kg/m | 457.01
| Main bar 12 mm dia at 200 mm c/c Horizontally on bottom face | 54 | 9.64 | 0.88171 | kg/m | 458.98
| Dist bar 12 mm dia at 200 mm c/c Horizontally on bottom face | 44 | 11.78 | 0.88171 | kg/m | 457.01
Haunch Bar
| Haunch bar 12 mm dia at 200 mm c/c diagonally | 54 | 1.2 | 0.88171 | kg/m | 57.13
| Haunch bar 12 mm dia at 200 mm c/c diagonally | 44 | 1.2 | 0.88171 | kg/m | 46.55
|  |  |  | Sub Total |  | 1935.66 | kg
Component: Roughing Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
Long Walls Outer
| Main bar inner 12 mm Ø at 125 mm c/c Vertically on inner face | 27 | 10.88 | 0.88171 | kg/m | 259.01
| Dist bar 10 mm Ø at 250 mm c/c Horizontally on inner face | 86 | 2.38 | 0.6123 | kg/m | 125.33
| Main bar 12 mm Ø 200 mm c/c Vertically outer face | 17 | 10.88 | 0.88171 | kg/m | 163.08
| Dist bar 10 mm Ø at 250 mm c/c Horizontally on outer face | 86 | 2.38 | 0.6123 | kg/m | 125.33
Long Walls Inner
| Main bar 12 mm Ø 200 mm c/c Vertically both face | 17 | 10.88 | 0.88171 | kg/m | 163.08
| Dist bar 10 mm Ø at 250 mm c/c Hor both face | 86 | 2.38 | 0.6123 | kg/m | 125.33
|  |  |  | Sub Total |  | 961.16 | kg
Short Wall
| Main bar inner 12 mm Ø at 200 mm c/c Horizontaly on inner face | 17 | 8.54 | 0.88171 | kg/m | 128.01
| Dist bar 10 mm Ø at 250 mm c/c vertically on inner face | 62 | 2.78 | 0.6123 | kg/m | 105.54
| Main bar inner 12 mm Ø at 200 mm c/c horizontally on outer face | 17 | 8.54 | 0.88171 | kg/m | 128.01
| Dist bar 10 mm Ø at 250 mm c/c Vertically on outer face | 62 | 2.78 | 0.6123 | kg/m | 105.54
Inner short walls
| Main bar inner 12 mm Ø at 200 mm c/c Horizontaly on inner face | 33 | 8.54 | 0.88171 | kg/m | 248.48
| Dist bar 10 mm Ø at 250 mm c/c vertically on inner face | 122 | 2.78 | 0.6123 | kg/m | 207.67
|  |  |  | Sub Total |  | 923.25 | kg
| Corner bars 12 mm dia @ 200 mm c/c | 36 | 3.584 | 0.88171 | kg/m | 113.76
Channel
| Main bar 10 mm @ 150 mm c/c | 104 | 0.45 | 0.6123 | kg/m | 28.66
| Distribution bar 10 mm @ 100 mm c/c | 47 | 7.54 | 0.6123 | kg/m | 216.99
Slab of Valve Chamber
| Inlet VC Long side | 9 | 1.2 | 0.6123 | kg/m | 6.61
| Short side | 8 | 1.4 | 0.6123 | kg/m | 6.86
| Outlet VC one number Long side | 9 | 1.2 | 0.6123 | kg/m | 6.61
| Short side | 8 | 1.4 | 0.6123 | kg/m | 6.86
|  |  |  | Sub Total |  | 386.35
|  |  |  | Sub Total |  | 4206.42 | kg
| Deduct manhole | 2 | 0.2826 |  |  | 0.57
| Net Reinforcement |  |  |  |  | 4205.85 | kg
10 | Brick Masonry Work in 1:6 Cement Sand mortar
| Inlet VC Long Wall | 2 | 1.43 | 0.23 | 0.68 | 0.45
| Short wall | 1 | 1 | 0.23 | 0.68 | 0.16
| Outlet VC Long Wall | 2 | 1.43 | 0.23 | 0.68 | 0.45
| Short wall | 1 | 1 | 0.23 | 0.68 | 0.16
|  |  |  | Total |  | 1.22
Component: Roughing Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
11 | 12.5 mm Thick Cement Sand Plaster in
1:3 Mortar with 2% Water Proof
Compound
| Long Walls-outer side | 2 | 9.68 |  | 1.4 | 27.1
| Short Wall Outer | 2 | 7.54 |  | 1.4 | 21.11
| Short Wall inner | 20 | 3.5 |  | 1.6 | 112
| Long Wall Inner | 4 | 2 |  | 1.6 | 12.8
|  | 8 | 3 |  | 1.6 | 38.4
|  | 8 | 0.8 |  | 1.6 | 10.24
| Base of water chamber | 2 | 3.5 | 0.8 |  | 5.6
Inlet and Outlet Channel
| outer base | 2 | 7.54 | 0.3 |  | 4.52
| wall | 2 | 7.54 |  | 0.375 | 5.66
| inner base | 2 | 7.54 |  | 0.3 | 4.52
| Slab cover of Inlet VC | 1 | 1.2 | 1 |  | 1.2
| Slab cover of Outlet VC | 1 | 1.2 | 1 |  | 1.2
| sides Inlet VC | 2 | 4.32 | 0.1 |  | 0.86
| sides outlet VC | 2 | 4.32 | 0.1 |  | 0.86
| Top of walls- long | 2 | 9.68 | 0.18 |  | 3.48
| Central long | 1 | 9.68 | 0.18 |  | 1.74
| Outershort | 2 | 7.54 | 0.18 |  | 2.71
| Inner Short | 8 | 3.5 | 0.075 |  | 2.1
| Inlet and outlet channel top | 2 | 7.54 | 0.075 |  | 1.13
| Valve Chambers long wall outside | 2 | 1.43 |  | 0.6 | 1.72
| Short Wall out side | 1 | 1.46 |  | 0.6 | 0.88
| Inner part of - long wall | 2 | 1.2 |  | 0.68 | 1.63
| Short wall | 1 | 1 |  | 0.68 | 0.68
| Slab cover inlet | 1 | 1.43 | 1.46 |  | 2.09
| Valve Chambers long wall outside | 2 | 1.43 |  | 0.6 | 1.72
| Short Wall out side | 1 | 1.46 |  | 0.6 | 0.88
| Inner part of chamber-long wall | 2 | 1.2 |  | 0.68 | 1.63
| Short wall | 1 | 1 |  | 0.68 | 0.68
| Slab cover outlet | 1 | 1.43 | 1.46 |  | 2.09
|  |  |  | Sub Total |  | 271.23 | m2
| Deduction manhole opening | 2 | 0.2826 |  | 0.1 | 0.06
|  |  |  | Total |  | 271.17 | m2
12 | 20 mm Thick Cement Sand Plaster in
| 1:4 Mortar in Base Slab | 2 | 2 | 3.5 |  | 14
| Compartment 1 | 2 | 3 | 3.5 |  | 21
| Compartment 2 | 2 | 3 | 3.5 |  | 21
| Compartment 3 | 4 | 0.8 | 3.5 |  | 11.2
[5 empty] | Total | 67.2 | m2
Component: Roughing Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
13 | 3 mm Thick Punning in 1: 1 Cement | inner plastered surfaces of HRF compartments
| Sand Mortar |  |  |  |  | 250.76 | m2
14 | Two Coat of Enamel Paint of | inner plastered surfaces of HRF compartments |  |  |  | 78.53 | m2
Appropriate Colour on Exposed
Surface of Tank
15 | Preparation and Placing of 40-20 mm
dia. Gravel Filter Media as per
| Specification | 2 | 2 | 3.5 | 1.5 | 21 | m3
16 | Preparation and Placing of 20-10 mm
dia. Gravel Filter Media as per
| Specification | 2 | 3 | 3.5 | 1.5 | 31.5 | m3
17 | Preparation and Placing of 04-10 mm
dia. Gravel Filter Media as per
| Specification | 2 | 3 | 3.5 | 1.5 | 31.5 | m3
18 | Installation of 5 inch dia. Pipe
Pipe Pieces and Fittings for Inlet,
Outlet and W/O Complete as per
| Drawing and Specification | 1 |  |  |  | 1 | Job
19 | Standard Manhole Cover (60cm dia)
including M.S. Angle of 1.5" in
Size including Fixing all Complete as
| per Drawing and Specification | 2 |  |  |  | 2 | Nos.
Component: Slow Sand Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
1 | Site Clearence | 1 | 14 | 14 |  | 196 | m 2
2 | Earth Work in Excavation in
Foundation in Boulder Mixed Soil
| Levelling work | 1 | 13.68 | 13.92 | 0.3 | 57.13
| SSF | 1 | 13.68 | 13.92 | 1.59 | 302.78
| Inlet VC | 1 | 1.83 | 1.86 | 1.59 | 5.41
| Outlet VC | 2 | 1.83 | 1.86 | 1.59 | 10.82
| Clear water chamber | 1 | 1.64 | 2.08 | 1.59 | 5.42
|  |  |  | Total |  | 381.56 | m 3
3 | Earth Filling in Foundation
| SSF Long wall | 2 | 13.68 | 0.6 | 1 | 16.42
| SSF short wall | 2 | 12.96 | 0.6 | 1 | 15.55
|  |  |  | Total |  | 31.97 | m 3
4 | Stone Soling with sand packing on
| Base of Foundation, SSF | 1 | 13.8 | 13.62 | 0.2 | 37.59
| Inlet VC | 1 | 1.73 | 1.76 | 0.2 | 0.61
| Outlet VC | 2 | 1.73 | 1.76 | 0.2 | 1.22
| Clear water chamber | 1 | 1.64 | 2.08 | 0.2 | 0.68
|  |  |  | Total |  | 40.1 | m 3
5 | Laying of P.C.C. 1:3:6 on Base of
| Foundation SSF | 1 | 13.8 | 13.62 | 0.1 | 18.8
| Inlet VC | 1 | 1.73 | 1.76 | 0.1 | 0.3
| Outlet VC | 2 | 1.73 | 1.76 | 0.1 | 0.61
| Clear water chamber | 1 | 1.64 | 2.08 | 0.1 | 0.34
|  |  |  | Total |  | 20.05 | m 3
6 | Laying of One Layer Tarfelt Over
| Lean Concrete SSF | 1 | 13.8 | 13.62 |  | 187.96
| Clear water chamber | 1 | 1.64 | 2.08 |  | 3.41
|  |  |  | Total |  | 191.37 | m 3
7 | P.C.C (1: 1.5:3) Works for R.C.C
SSF
| Base Slab | 1 | 13.38 | 13.62 | 0.29 | 52.85
| Outer Long Wall | 2 | 12.48 | 0.24 | 1.5 | 8.99
| Outer Long Wall | 2 | 12.48 | 0.15 | 1.3 | 4.87
| Inner Long Wall | 1 | 12.48 | 0.24 | 1.5 | 4.49
| Inner Long Wall | 1 | 12.48 | 0.15 | 1.3 | 2.43
| Short Wall | 4 | 6 | 0.24 | 1.5 | 8.64
| Short Wall | 4 | 6 | 0.15 | 1.3 | 4.68
| Channel | 1 | 12.24 | 0.3 | 0.075 | 0.28
|  | 1 | 12.24 | 0.15 | 0.075 | 0.14
| Scum collector | 1 | 12.24 | 0.3 | 0.075 | 0.28
|  | 1 | 12.24 | 0.15 | 0.075 | 0.14
Component: Slow Sand Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
| Clear water chamber, base | 1 | 1.59 | 1.98 | 0.29 | 0.91
| Long Wall | 2 | 1.44 | 0.24 | 2.8 | 1.94
| Short Wall | 1 | 1.68 | 0.24 | 2.8 | 1.13
| Slab cover of Inlet VC | 1 | 1.66 | 1.46 | 0.1 | 0.24
| Slab cover of Outlet VC | 2 | 1.66 | 1.46 | 0.1 | 0.48
| Slab cover of Clear water chamber | 1 | 1.44 | 2.16 | 0.1 | 0.31
|  |  |  | Sub Total |  | 92.8 | m 3
| Deduct manhole opening | 4 | 0.2826 |  | 0.1 | 0.11
|  |  |  | Total |  | 92.69 | m 3
8 | Centring and Shuttering Works for
P.C.C. and R.C.C Works
SSF
| Base Slab Long wall | 2 | 13.38 |  | 0.39 | 10.44
| Short Wall | 2 |  | 13.62 | 0.39 | 10.62
| Outer part of Outer Long Wall | 2 | 12.48 |  | 2.8 | 69.89
| Inner part of Outer Long Wall | 2 | 12 |  | 2.8 | 67.2
| Inner Long Wall | 2 | 12 |  | 2.8 | 67.2
| Outer part of Short Wall | 2 | 12.48 |  | 2.8 | 69.89
| Inner part of Short Wall | 4 | 6 |  | 2.8 | 67.2
| Channel | 1 | 12.24 | 0.3 | 0.375 | 1.38
| Scum collector | 1 | 12.24 | 0.3 | 0.375 | 1.38
| Clear water chamber | 2 | 1.44 |  | 0.39 | 1.12
| Short Wall | 1 | 2.16 |  | 0.39 | 0.84
| Long Wall | 2 | 1.2 |  | 2.8 | 6.72
| Short Wall | 1 | 1.68 |  | 2.8 | 4.7 | m 2
| Slab cover of Inlet VC | 1 | 1.2 | 1 |  | 1.2
| Slab cover of Outlet VC | 2 | 1.2 | 1 |  | 2.4
| Slab cover of Clear water chamber | 1 | 1.2 | 1.2 |  | 1.44
| sides Inlet VC | 2 | 4.32 | 0.1 |  | 0.86
| sides outlet VC | 4 | 4.32 | 0.1 |  | 1.73
| sides CWC | 2 | 4.56 | 0.1 |  | 0.91
|  |  |  | Sub Total |  | 387.12
| Deduct manhole opening | 4 | 0.2826 |  |  | 1.13
|  |  |  | Total |  | 385.99
9 | Reiforcement Works with Deformed
bars Including Supplying,Cutting,
Bending and Placing in Position
Component: Slow Sand Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
Base Slab
| Main bar 16 mm dia at 175 mm c/c Horizontally on top face | 78 | 15.22 | 1.5675 | kg/m | 1860.86
| Dist bar 10 mm dia at 200 mm c/c Horizontally on top face | 70 | 14.38 | 0.6123 | kg/m | 616.34
| Main bar 16 mm dia at 175 mm c/c Horizontally on bottom face | 78 | 15.22 | 1.5675 | kg/m | 1860.86
| Dist bar 10 mm dia at 200 mm c/c Horizontally on bottom face | 70 | 14.38 | 0.6123 | kg/m | 616.34
Haunch Bar
| Haunch bar12 mm dia200 mm c/c diagonally | 254 | 1.2 | 0.88171 | kg/m | 268.75
| Haunch bar12 mm dia 200 mm c/c diagonally | 130 | 1.2 | 0.88171 | kg/m | 137.55
|  |  |  | Sub Total |  | 5360.7 | kg
Long Walls
| Main bar 12 mm dia 140 mm c/c ver IF | 180 | 2.39 | 0.88171 | kg/m | 379.31
| Main bar 12 mm dia 140 mm c/c ver IF | 180 | 1.9 | 0.88171 | kg/m | 301.55
| Dist bar 10 mm dia 200 mm c/c Hor IF | 30 | 13.48 | 0.6123 | kg/m | 247.61
| Main bar 12 mm dia 280 mm c/c ver OF | 91 | 3.69 | 0.88171 | kg/m | 296.07
| Dist bar 10 mm dia at 200 mm c/c Hor OF | 30 | 13.48 | 0.6123 | kg/m | 247.61
[6 empty] | 1472.15 | kg
Inner Long Walls
| Main bar 12 mm dia at 120 mm c/c vertically on both face | 209 | 3.69 | 0.88171 | kg/m | 679.99
| Dist bar 10 mm dia at 200 mm c/c Horizontally on both face | 30 | 13.48 | 0.6123 | kg/m | 247.61
[6 empty] | 927.6 | kg
Short Wall
| Main bar 12 mm dia at 140 mm c/c vertically on inner face | 183 | 2.39 | 0.88171 | kg/m | 385.63
| Main bar 12 mm dia at 140 mm c/c vertically on inner face | 183 | 1.9 | 0.88171 | kg/m | 306.57
| Dist bar 10 mm dia at 200 mm c/c Horizontally on inner face | 30 | 13.72 | 0.6123 | kg/m | 252.02
| Main bar 12 mm dia at 140 mm c/c vertically on outer face | 183 | 2.39 | 0.88171 | kg/m | 385.63
| Main bar 12 mm dia at 280 mm c/c vertically on outer face | 92 | 1.9 | 0.88171 | kg/m | 154.12
| Dist bar 10 mm dia at 200 mm c/c Horizontally on outer face | 30 | 13.72 | 0.6123 | kg/m | 252.02
[6 empty] | 1735.99 | kg
| Corner bars 12 mm dia @ 200 mm c/c | 60 | 3.824 | 0.88171 | kg/m | 202.3
Channel
| Main bar 12 mm @ 150 mm c/c | 83 | 0.95 | 0.6123 | kg/m | 48.28
| Distribution bar 12 mm @ 100 mm c/c | 6 | 12.24 | 0.6123 | kg/m | 44.97
| Scum collector | 83 | 0.95 | 0.6123 | kg/m | 48.28
|  | 6 | 12.48 | 0.6123 | kg/m | 45.85
| Clear water chamber base all | 38 | 1.59 | 0.6123 | kg/m | 37
| Long Wall | 90 | 3.04 | 0.6123 | kg/m | 167.53
| Short Wall | 23 | 3.28 | 0.6123 | kg/m | 46.19
Slab of Valve Chamber
| Inlet VC Long side | 9 | 1.63 | 0.6123 | kg/m | 8.98
| Short side | 9 | 1.66 | 0.6123 | kg/m | 9.15
| Outlet VC two numbers Long side | 18 | 1.63 | 0.6123 | kg/m | 17.96
| Short side | 18 | 1.66 | 0.6123 | kg/m | 18.3
[6 empty] | 694.79 | kg
|  |  |  | Sub Total |  | 10191.23
Deduct
Inner Long Walls
| Main bar 12 mm dia at 240 mm c/c vertically on both face | 105 | 1.3 | 0.88171 | kg/m | 120.35
Short wall outer face
| Main bar 12 mm dia at 280 mm c/c vertically on outer face | 92 | 1.3 | 0.88171 | kg/m | 105.45
|  |  |  | Total Deduction |  | 225.8
| Net Reinforcement |  |  |  |  | 9965.43 | kg
Component: Slow Sand Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
10 | Brick Masonry Work in
1:6 Cement Sand mortar
| Inlet VC Long Wall | 2 | 1.43 | 0.23 | 2.29 | 1.51
| Short wall | 1 | 1 | 0.23 | 2.29 | 0.53
| Outlet VC Long Wall | 4 | 1.43 | 0.23 | 2.29 | 3.01
| Short wall | 2 | 1 | 0.23 | 2.29 | 1.05
|  |  |  | Total |  | 6.1
11 | 12.5 mm Thick Cement Sand Plaster
in 1:3 Mortar with 2% Water Proof
Compound SSF
| Outer part of Outer Long Wall | 2 | 12.48 |  | 2 | 49.92
| Inner part of Outer Long Wall | 2 | 12 |  | 2.8 | 67.2
| Inner Long Wall | 2 | 12 |  | 2.8 | 67.2
| Outer part of Short Wall | 2 | 12.72 |  | 2 | 50.88
| Inner part of Short Wall | 4 | 6 |  | 2.8 | 67.2
Top
| Long wall | 2 | 12.48 | 0.24 |  | 5.99
| short wall | 4 | 6 | 0.24 |  | 5.76
| Inner wall | 1 | 12.48 | 0.24 |  | 3
| Channel | 1 | 12.24 | 0.525 |  | 6.43
|  | 1 | 12.24 | 0.45 |  | 5.51
| Scum collector | 1 | 12.24 | 0.525 |  | 6.43
|  | 1 | 12.24 | 0.45 |  | 5.51
Clear water chamber
| Outer part of Long Wall | 2 | 1.44 |  | 2 | 5.76
| Inner part of Long Wall | 2 | 1.2 |  | 2.8 | 6.72
| Outer part of Short Wall | 1 | 1.68 |  | 2 | 3.36
| Inner part of Short Wall | 1 | 1.2 |  | 3 | 3.6
Top
| Long wall | 2 | 1.44 | 0.24 |  | 0.69
| short wall | 1 | 1.2 | 0.24 |  | 0.29
Valve chambers
| Outlet Outer part of Long Wall | 4 | 1.43 |  | 0.5 | 2.86
| Inner part of Long Wall | 4 | 1.2 |  | 1.79 | 8.59
| Outer part of Short Wall | 2 | 1.43 |  | 0.3 | 0.86
| Inner part of Short Wall | 2 | 1 |  | 1.79 | 3.58
| Inlet Outer part of Long Wall | 2 | 1.43 |  | 0.5 | 1.43
Component: Slow Sand Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
| Inner part of Long Wall | 2 | 1.68 |  | 1.79 | 6.01
| Outer part of Short Wall | 1 | 1.46 |  | 0.3 | 0.44
| Inner part of Short Wall | 1 | 1 |  | 1.79 | 1.79
Top
| Long wall | 8 | 1.43 | 0.24 |  | 2.75
| short wall | 8 | 1 | 0.24 |  | 1.92
Slabs
| Slab cover of Inlet VC | 1 | 1.2 | 1.46 |  | 1.75
| Slab cover of Outlet VC | 2 | 1.2 | 1.46 |  | 3.5
| Slab cover of Clear water chamber | 1 | 1.44 | 2.16 |  | 3.11
400.04
| Deduct manhole | 4 | 0.2826 |  |  | 1.13
|  |  |  | Total |  | 398.91 | m 2
12 | 20 mm Thick Cement Sand Plaster in
1:4 Mortar in Base Slab
| SSF | 2 | 12 | 6 |  | 144
| Clear water chamber | 1 | 1.2 | 1.2 |  | 1.44
|  |  |  | Total |  | 145.44 | m 2
13 | 3 mm Thick Punning in 1: 1 Cement
| Sand Mortar | inner plastered surfaces of SSF and CWC |  |  |  | 357.36
| Channel | 1 | 12.24 | 0.3 |  | 3.67
| Scum collector | 1 | 12.24 | 0.3 |  | 3.67
|  |  |  | Total |  | 364.7 | m 2
14 | Smoothly Finished Local Brick
Masonry Support in 1:4 Cement
Sand Mortar 2 m C/C
| Manifold | 62 | 0.45 | 0.23 | 0.2 | 1.28
| Laterals, | 202.5 | 0.45 | 0.23 | 0.2 | 4.19
|  |  |  | Total |  | 5.47 | m 3
15 | HDPE Perforated Pipe of
| Manifold 160 mm dia.10 kg/cm2 | 2 | 12.24 |  |  | 24.48 | m
| Laterals 63 mm dia.10 kg/cm2 | 30 | 5.42 |  |  | 162.6 | m
16 | Preparation and Placing of Gravel
| Filter Media 3 to 6 mm as per Spec. | 2 | 12 | 6 | 0.2 | 28.8 | m 3
17 | Preparation and Placing of Gravel
| Filter Media 6 to 20 mm as per Spec. | 2 | 12 | 6 | 0.15 | 21.6 | m 3
18 | Preparation and Placing of Gravel
| Filter Media 20 to 40 mm as per Spec. | 2 | 12 | 6 | 0.15 | 21.6 | m 3
19 | Preparation and Placing of Filter
| Sand as per Specification | 2 | 12 | 6 | 1 | 144 | m 3
Component: Slow Sand Filter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
20 | Two Coat of Enamel Paint of
| Appropriate Colour on Exposed | Outer plastered surfaces of SSF and CWC
| Surface of Tank |  |  |  |  | 129.37 | m 2
21 | Installation charges of 5 inch dia. Pipe
Pieces and Fittings for Inlet, Outlet
and W/O Complete as per Drawing
| and Specification | lumpsum |  |  |  | L.S.
22 | Connection of laterals with manifold and
Installation charges of 160 mm dia.HDPE
| dia.HDPE Pipe for Manifold | lumpsum |  |  |  | L.S.
23 | Preparation of holes and Installation
charges of 63 mm dia.HDPE Pipe for
| Laterals | lumpsum |  |  |  | L.S.
24 | Standard Manhole Cover (60cm dia)
including M.S. Angle of 1.5" in
Size including Fixing all Complete as
| per Drawing and Specification | 4 |  |  |  | 4 | Nos.
Component: Sand Wash Platform
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
1 | Site Clearence | 1 | 4 | 4 |  | 16 | m 2
2 | Earth Work Excavation in
| Foundation in Boulder Mixed Soil | 1 | 4 | 4 | 0.35 | 5.6 | m 3
3 | Stone Soling in Base of Foundation | 1 | 4 | 4 | 0.2 | 3.2 | m 3
4 | Laying of P.C.C. 1:3:6 on Base of
| Foundation | 1 | 4 | 4 | 0.1 | 1.6 | m 3
5 | M 15 P.C.C. (1:2:4) in Panel of
| 2.0 m x 1.0 m | 1 | 4 | 4 | 0.1 | 1.6 | m 3
6 | 20 mm Thick Cement Sand Plaster in
| 1:4 Mortar in Base Slab | 1 | 4 | 4 |  | 16 | m 2
7 | 3 mm Thick Punning in 1: 1 Cement
| Sand Mortar | 1 | 4 | 4 |  | 16 | m 2
Component: Disinfection Chamber
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
1 | Site Clearence | 1 | 2 | 2 |  | 4 | m 2
2 | Earth Work in Excavation in
| Foundation in Boulder Mixed Soil | 1 | 1.5 | 1.5 | 0.4 | 0.9 | m 3
3 | Boulder Soling with Sand packing | 1 | 1.5 | 1.5 | 0.15 | 0.34 | m 3
4 | P.C.C (1: 2 : 4) on Base | 1 | 1.5 | 1.5 | 0.1 | 0.23
| on top of wall | 1 | 0.54165 |  | 0.05 | 0.03
|  |  |  | Total |  | 0.26 | m 3
5 | Brick Masonry Work in
| 1:4 Cement Sand mortar | 1 | 0.54165 | 0.23 | 0.45 | 0.24 | m 3
6 | Supply of 500 litres tank
| tank with necessary fittings | 1 |  |  |  | 1 | job
7 | Installation of Pipe Pieces and
Fittings for Inlet, Outlet and W/O
Complete as per Drawing and
| Specification for 500 litres tank | 1 |  |  |  | 1 | job
Component: Site Development Work (Total Length 10 m)
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
1 | Site Clearence | 1 | 10 | 1.6 |  | 16 | m 2
2 | Earth Work Excavation in Boulder
and Gravel Mixed Soil
| Levelling of the Ground | 1 | 10 | 1.6 | 0.15 | 2.4
| Side Wall | 1 | 10 | 0.35 | 0.3 | 1.05
| Drainage | 1 | 10 | 0.45 | 0.3 | 1.35
[6 empty] | 4.8 | m 3
3 | Earth Filling with Compaction
| Layer with Sprinkling of Water | 1 | 10 | 1 | 0.1 | 1 | m 3
4 | Dry Stone Soling in Foot Path | 1 | 10 | 1 | 0.15 | 1.5
|  |  |  | Total |  | 1.5 | m 3
5 | P.C.C. (1:3:6) in Drain | 1 | 10 | 0.8 | 0.05 | 0.4 | m 3
6 | Brick Masonry Work with 1:6
| Cement Mortar in walls of Drain | 1 | 10 | 0.23 | 0.15 | 0.35
| Base | 1 | 10 | 0.8 | 0.25 | 2
| walls | 1 | 10 | 0.23 | 0.25 | 0.58
|  |  |  | Total |  | 2.93 | m 3
7 | 12.5 mm Thick Cement Sand Plaster
| in 1:4 Mortar | 1 | 10 | 1.06 |  | 10.6 | m 2
Component: BARBED WIRE FENCING (Total Fencing Length 24 m)
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
BARBED WIRE FENCING
1 | Site Clearance |  |  |  |  | L.S.
2 | Earthwork in excavation pillars | 16 | 0.35 | 0.35 | 0.6 | 1.18
| walls | 10 | 1.5 | 0.35 | 0.6 | 3.15
[6 empty] | 4.33 | m³
3 | Dry stone soling with sand pillars | 16 | 0.35 | 0.35 | 0.1 | 0.2
| walls | 10 | 1.5 | 0.35 | 0.1 | 0.53
[6 empty] | 0.73 | m³
4 | PCC (1:2:4) for anchor blocks | 16 | 0.35 | 0.35 | 0.5 | 0.98 | m³
5 | Stone masonry (1:6) cement mortar Pillars | 16 | 0.35 | 0.35 | 0.5 | 0.98
| walls | 10 | 1.5 | 0.35 | 0.7 | 3.68
[6 empty] | 4.66 | m³
6 | Barbed wire fencing (16+1: one more lengths of barbed
| wire to be anchored on entrance gate). | 119 | 1.5 |  |  | 178.5
| Cross Barbed Wire [L = (1.5² + 1.5²)½] | 34 | 2.12 |  |  | 72.08
[6 empty] | 250.58 | m
7 | 6 mm ø mild steel rod for hooks, 650 mm long each | 36 | 0.65 | 0.22 | kg/m | 5.15 | kg
8 | M.S. 40 x 40 x 6 angle bar, 2.5 m long | 16 | 2.8 | 3.5 | kg/unit | 156.8 | kg
Component: ENTRANCE GATE
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
1 | Site Clearance |  |  |  |  | L.S.
2 | Earthwork in excavation in foundation | 2 | 0.6 | 0.6 | 0.6 | 0.43 | m³
3 | Boulder masonry iin (1:6) cement mortar for Pillar
| In foundation | 2 | 0.6 | 0.6 | 0.6 | 0.43
| Above Ground | 2 | 0.45 | 0.45 | 1.6 | 0.65
[6 empty] | 1.08 | m³
4 | Cement pointing in (1:3) for Pillars | 8 | 0.45 | - | 1.6 | 5.76
| On top | 2 | 0.45 | 0.45 | - | 0.41
| Deduct two sides | 2 | 0.45 | - | 0.6 | -0.54
[6 empty] | 5.63 | m²
5 | 25 x 25 x 3 m Size Mild Steel angle frames gate with Iron
Grill shutter (0.95 x 1.5 m size) all complete including
| fixing no. | 1 |  |  |  | 1 | No.
6 | Enamel Painting for Gate | 1 | 0.95 | - | 1.5 | 1.43 | m²
Component: Watchman Quarter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
1 | Site Clearance | 1 | 8 | 4.2 |  | 33.6 | m 2
2 | Earthwork in excavation for foundation
in hard soil for
| L/W | 2 | 6.4 | 0.95 | 0.85 | 10.34
| S/W | 2 | 3.3 | 0.95 | 0.85 | 5.33
| Wall between kitchen & verandas | 1 | 2.8 | 0.95 | 0.85 | 2.26
| Apron | 1 | 20 | 0.38 | 0.2 | 1.52
| Drain | 1 | 22 | 0.4 | 0.3 | 2.64
|  |  |  | Total |  | 22.09 | m 3
3 | 10 cm earth filling for
| Bedroom | 1 | 3.3 | 2.4 | 0.1 | 0.79
| kitchen | 1 | 2.05 | 1.75 | 0.1 | 0.36
| Verandah | 1 | 1.75 | 1.35 | 0.1 | 0.24
|  |  |  | Total |  | 1.39 | m 3
4 | 15 cm boulder soling
| in floor |  | Details as per Item no. 3 |  |  | 1.39
| in appron | 1 | 20 | 0.38 | 0.1 | 0.76
| in drain | 1 | 22 | 0.4 | 0.1 | 0.88
| In foundation | 1 | 18.5 | 0.95 | 0.15 | 2.64
|  |  |  | Total |  | 5.67 | m 3
5 | Laying of 500 gauge polythene sheet | 1 | 5.95 | 4.2 | - | 24.99
6 | Stone masonry work in 1:6 cement sand mortar
for foundation
| First footing | 1 | 17.6 | 0.75 | 0.2 | 2.64
| Second footing | 1 | 17 | 0.55 | 0.3 | 2.81
| Wall up to plinth | 1 | 17 | 0.35 | 0.35 | 2.08
| First step | 1 | 1.75 | 0.45 | 0.15 | 0.12
| Second step | 1 | 1.75 | 0.35 | 0.15 | 0.09
|  |  |  | Total |  | 7.74 | m 3
7 | P.C.C. 1:2:4 in DPC | 2 | 5.5 | 0.35 | 0.05 | 0.19
| Short wall | 2 | 3.3 | 0.35 | 0.05 | 0.12
| Wall between kitchen & verandas | 1 | 2.8 | 0.23 | 0.05 | 0.03
| Lintel over D1 | 1 | 1.2 | 0.35 | 0.1 | 0.04
| Lintel over D2 | 1 | 1.05 | 0.23 | 0.1 | 0.02
| Lintel over W1 | 2 | 1.35 | 0.35 | 0.1 | 0.09
| Lintel over W2 | 1 | 1.2 | 0.35 | 0.1 | 0.04
| Lintel over varandah | 1 | 2.05 | 0.35 | 0.15 | 0.11
| PCC anchor block for holdfast | 20 | 0.3 | 0.1 | 0.1 | 0.06
| Steps | 1 | 1.75 | 0.75 | 0.05 | 0.07
50 mm P.C.C. for
| Flooring | 1 | 4.6 | 3.3 | 0.05 | 0.76
| Apron | 1 | 20.3 | 0.38 | 0.05 | 0.39
| Drain | 1 | 22 | 0.4 | 0.05 | 0.44
P.C.C. for R.C.C. work
| Roof Slab | 1 | 6.15 | 4.8 | 0.1 | 2.95
|  |  |  | Total |  | 5.31 | m 3
Component: Watchman Quarter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
8 | Stone masonry work in 1:6 cement
| sand mortar for drain | 2 | 22 | 0.1 | 0.1 | 0.44
Super structure
| Main wall | 1 | 15.8 | 0.35 | 2.8 | 15.48
| Partition wall | 1 | 1.75 | 0.23 | 2.8 | 1.13
| Partition wall | 1 | 2.28 | 0.23 | 0.79 | 0.41
|  |  |  | Sub Total |  | 17.46 | m 3
| Deductions Main entrance | 1 | 1.75 | 0.35 | 2.13 | 1.3
| Door D1 | 1 | 0.9 | 0.35 | 2.13 | 0.67
| Door D2 | 1 | 0.76 | 0.23 | 2.13 | 0.37
| Window W1 | 2 | 1.05 | 0.35 | 1.2 | 0.88
| Window W2 | 1 | 0.9 | 0.35 | 1.2 | 0.38
| Lintel over D1 | 1 | 1.2 | 0.35 | 0.1 | 0.04
| Lintel over D2 | 1 | 1.05 | 0.23 | 0.1 | 0.02
| Lintel over W1 | 2 | 1.35 | 0.35 | 0.1 | 0.09
| Lintel over W2 | 1 | 1.2 | 0.35 | 0.1 | 0.04
| Lintel over varandah | 1 | 2.05 | 0.35 | 0.15 | 0.11
| PCC anchor block for holdfast | 20 | 0.3 | 0.1 | 0.1 | 0.06
|  |  |  | Sub Total |  | 3.96 | m 3
|  |  |  | Total |  | 13.5 | m 3
9 | Centering & Shuttering work for PCC
| Anchor blocks for holdfast | 40 | 0.3 | - | 0.1 | 1.2
| sand mortar for drain | 2 | 22 |  | 0.1 | 4.4
| Lintel over D1 Base | 1 | 1.2 | 0.35 |  | 0.42
| Sides | 2 | 1.2 |  | 0.1 | 0.24
| Lintel over D2 Base | 1 | 1.05 | 0.23 |  | 0.24
| Sides | 2 | 1.05 |  | 0.1 | 0.21
| Lintel over W1 Base | 1 | 1.35 | 0.35 |  | 0.47
| Sides | 2 | 1.35 |  | 0.1 | 0.27
| Lintel over W2 Base | 1 | 1.2 | 0.35 |  | 0.42
| Sides | 2 | 1.2 |  | 0.1 | 0.24
| Lintel over varandah Base | 1 | 2.05 | 0.35 |  | 0.72
| Sides | 2 | 2.05 |  | 0.15 | 0.62
| Side of wall | 1 | 23.3 |  | 0.05 | 1.17
| Side of apron | 2 | 21.2 |  | 0.05 | 2.12
| Side of drain | 2 | 23 |  | 0.05 | 2.3
| Slab Base | 1 | 6.15 | 4.3 |  | 26.45
| Sides | 1 | 20.9 |  | 0.1 | 2.09
|  |  |  | Total |  | 43.58 | m 2
10 | Reinforcement with deformend bars
including cutting, bending and placing in
position
| Main bar 12 mm dia @ 175 mm c/c | 36 | 5.9 | 0.88 |  | 186.91
| Distribution bar 10 mm dia @ 200 mm c/c | 23 | 6.45 | 0.62 |  | 91.98
| corner reinforcement 10 mm dia | 80 | 1.2 | 0.62 |  | 59.52
Component: Watchman Quarter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
Lintel bars over D1, D2, W1, W2
| Main bar 12 mm dia @ 100 mm c/c | 16 | 1.55 | 0.88 |  | 21.82
| Distribution bar 10 mm dia @ 150mm c/c | 40 | 0.35 | 0.62 |  | 8.68
| Lintel bars over varandah | 4
| Main bar 12 mm dia @ 175 mm c/c | 4 | 2.25 | 0.88 |  | 7.92
| Distribution bar 10 mm dia @ 150 mm c/c | 16 | 0.35 | 0.62 |  | 3.47
|  |  |  | Total |  | 380.3 | kg
11 | Salwood work for Chaukhats for
| Door D1 | 1 | 5.15 | 0.1 | 0.075 | 0.04
| Door D2 | 1 | 5.02 | 0.1 | 0.075 | 0.04
| Window W1 | 2 | 4.5 | 0.1 | 0.075 | 0.07
| Window W2 | 1 | 4.2 | 0.1 | 0.075 | 0.03
|  |  |  | Total |  | 0.18 | m 3
12 | 38 mm thick Local wood panalled shutters
| Door D1 | 1 | 0.76 |  | 2.07 | 1.57
| Door D2 | 1 | 0.64 |  | 2.07 | 1.32
|  |  |  | Total |  | 2.89 | m 2
13 | 38 mm thick Local wood glazed shutters
| Window W1 | 2 | 0.93 |  | 1.08 | 2.01
| Window W2 | 1 | 0.78 |  | 1.08 | 0.84
|  |  |  | Total |  | 2.85 | m 2
14 | 3 mm thick 1:1 cement sand punning
on floor and skirting for
| Bed room | 1 | 3.3 | 2.4 |  | 7.92
| Kitchen | 1 | 2.05 | 1.75 |  | 3.59
| Verandah | 1 | 1.75 | 1.35 |  | 2.36
| Add for door portion (sill) | 1 | 4.31 | 0.35 |  | 1.51
| Apron | 1 | 20 | 0.38 |  | 7.6
| Drain | 2 | 22 | 0.3 |  | 13.2
| Steps | 1 | 1.75 | 0.9 |  | 1.58
| Skirting | 1 | 20 |  | 0.15 | 3
|  |  |  | Total |  | 40.76 | m 2
15 | Cement plaster 12.5 mm thick
with 1:4 C/S mortar for
| Bed room | 1 | 3.3 | 2.4 |  | 7.92
| Kitchen | 1 | 2.05 | 1.75 |  | 3.59
| Verandah | 1 | 1.75 | 1.35 |  | 2.36
| Add for door portion (sill) | 1 | 4.31 | 0.35 |  | 1.51
| Apron | 1 | 20 | 0.38 |  | 7.6
| Drain | 2 | 22 | 0.3 |  | 13.2
| Steps | 1 | 1.75 | 0.75 |  | 1.31
| Steps | 2 | 22.8 | 0.15 |  | 6.84
on internal surfaces of walls for
| Bed room | 1 | 11.4 |  | 2.8 | 31.92
Component: Watchman Quarter
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
| Kitchen | 1 | 7.6 |  | 2.8 | 21.28
| Verandah | 1 | 1.75 |  | 2.8 | 4.9
on exterior surfaces of walls for
| Length | 1 | 18.5 |  | 2.8 | 51.8
|  |  |  | Sub Total |  | 154.23 | m 2
Deduction
| Door D1 | 1 | 0.76 |  | 2.13 | 1.62
| Door D2 | 1 | 0.64 |  | 2.13 | 1.36
| Window W1 | 2 | 0.93 |  | 1.2 | 2.23
| Window W2 | 1 | 0.78 |  | 1.2 | 0.94
|  |  |  | Sub Total |  | 6.15 | m 2
|  |  |  | Total |  | 148.08 | m 2
16 | 2 coats of white washing |  | Details as per Item no. 15 |  |  | 125.28 | m 2
| Deduction |  | Details as per Item no. 15 |  |  | 6.15
17 | Readymade enamel paint two coats |  |  | Total |  | 119.13 | m 2
with one coat of primer for
| Door D1 | 3 | 0.9 |  | 2.13 | 5.75
| Door D2 | 3 | 0.75 |  | 2.13 | 4.79
| Window W1 | 2 | 1.05 |  | 1.2 | 2.52
| Window W2 | 1 | 0.9 |  | 1.2 | 1.08
|  |  |  | Total |  | 14.14 | m 2
18 | Electrification and Sanitation | Lump sum |  |  |  | L.S
POUR FLUSH LATRINE
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
1 | Site Clearance | 1 | 3 | 2 |  | 6
[5 empty] | Total | 6 | m²
2 | Earthwork in excavation in hard soil in foundation for
| Long wall | 2 | 2.35 | 0.6 | 0.4 | 1.128
| Short wall | 2 | 1 | 0.6 | 0.4 | 0.48
|  | 1 | 0.25 | 0.6 | 0.4 | 0.06
| Pan | 1 | 1 | 0.625 | 0.3 | 0.1875
| Pit (Q = PI r² x h, r = 0.85 m) | 1 | Pi x 0.85² |  | 1.3 | 2.9519
| Pipe line | 2 | 4 | 0.3 | 0.5 | 1.2
[5 empty] | Total | 6.0074 | m³
3 | Stone soling with sand | 1 | 1.3 | 1 | 0.15 | 0.34061 | m³
4 | Dry stone masonry (Q = Pi*(R²-r²).h, R = 0.85, r = 0.50) | 2 | Pi x (0.85² - 0.50²) |  | 0.425 | 1.2622 | m³
5 | Stone masonry in mud mortar
| Foundation Long wall | 2 | 2.35 | 0.6 | 0.4 | 1.128
| Short wall | 2 | 1 | 0.6 | 0.4 | 0.48
| Super Structure Long wall | 2 | 2.2 | 0.45 | 2.28 | 4.5144
| Short wall | 1 | 1 | 0.45 | 1.9 | 0.855
| Wall | 1 | 0.25 | 0.45 | 2.57 | 0.28912
| Chamber | 1 | 1.8 | 0.3 | 0.475 | 0.2565
| Deduction Ventilation | 1 | 0.6 | 0.45 | 0.3 | -0.081
| Door | 1 | 0.75 | 0.45 | 2 | -0.675
[5 empty] | Total | 6.767 | m³
6 | Stone masonry in cement mortar1:4
| Pit (Q = Pi*(R²-r²).h, R = 0.85, r = 0.50) | 2 | Pi x (0.85² - 0.50²) |  | 1.1 | 3.267
| Chamber | 1 | 1 | 0.625 | 0.4 | 0.25
[5 empty] | Total | 3.517 | m³
7 | Squatting Pan | 1 | L.S. |  |  | 1 | No.
8 | PCC in slab cover for pits | 2 | Pi x (0.85² ) |  | 0.075 | 0.34061 | m³
| Chamber | 1 | 1 | 0.7 | 0.075 | 0.1703
[5 empty] | Total | 0.51091 | m³
9 | MS reinforcement 6 mm ø 100 mm c/c both ways for slab | 2x36 | 0.8x1.7 | 0.62 | kg/m | 59.5721
| 10 mm ø rod for ventilator as per drawing 20 cm long | 5 | 0.2 | 0.62 | kg/m | 0.62
[5 empty] | Total | 60.1921 | kgs
10 | 20 mm thick cement plaster (1:3) for squatting slab | 1 | 1.3 | 1 | - | 1.3 | m²
| Walls | 1 | 3 | - | 0.6 | 1.8
[5 empty] | Total | 3.1 | m²
11 | Cement Pointing work in 1:3 mortar | 1 | 4.75 |  | 1.5 | 7.125 | m²
12 | Woodwork for Door frame | 2 | 2 | 0.1 | 0.08 | 0.032
|  | 3 | 0.75 | 0.1 | 0.08 | 0.018
| Ventilator | 2 | 0.6 | 0.1 | 0.08 | 0.0096
|  | 2 | 0.3 | 0.1 | 0.08 | 0.0048
| Roof Rafter | 2 | 2.4 | 0.075 | 0.05 | 0.018
| Battens | 3 | 2.1 | 0.075 | 0.05 | 0.023625
[5 empty] | Total | 0.10603 | m³
13 | 32 mm thick door shutter with wooden frame
| & GI plain sheet one side | 1 | 1.53 | 0.63 | - | 0.9639 | m²
14 | Outlet Pipe (6 m long, 110 mm ø HDP pipe) | 2 | 6 |  |  | 12 | m
15 | Mosquito Screen | 1 | 0.65 | 0.3 | - | 0.195 | m²
16 | 26 gauge CGI sheet roofing | 1 | 2.5 | 2.4 | - | 6 | m²
Component: Retaining wall on Treatment Plant site
S.no. | Description of work | No. | Length | Breadth | Height | Quantity | Unit
1 | Site Clearance | 1 | 10 | 2 |  | 20 | m 2
2 | Earthwork in excavation for foundation
| in boulder mixed soil | 1 | 10 | 1 | 0.6 | 6 | m 3
3 | Earth filling in boulder mixed soil
| Foundation | 1 | 10 | 0.2 | 0.15 | 0.3
| Back Filling | 1 | 10 | 0.5 | 0.9 | 4.5
|  |  |  | Total |  | 4.8 | m 3
4 | Boulder soling with sand | 1 | 10 | 1.2 | 0.15 | 1.8 | m 3
5 | Stone masonry in 1:6 cement sand mortar
| Base | 1 | 10 | 1 | 0.3 | 3
| Rectangular part | 1 | 10 | 0.5 | 2 | 10
| Triangular Part | 1 | 10 | 0.25 |  | 2.5
|  |  |  | Total |  | 15.5 | m 3
6 | Cement pointing 1:3 on external
surface of wall
| Inclined face | 1 | 10 |  | 2.2 | 22
| Top | 1 | 10 | 0.5 |  | 5
|  |  |  | Total |  | 27 | m 2
Component: Catch Drain
S.no. | Description of work | No. | Length | Breadth | Height | Quantity | Unit
1 | E/W in excavation in Boulder mixed soil | 1 | 10 | 1 | 0.4 | 4 | m 3
2 | Boulder Soling with sand packing | 1 | 10 | 1 | 0.15 | 1.5 | m 3
3 | P.C.C. 1:2:4 | 1 | 10 | 0.3 | 0.075 | 0.23 | m 3
4 | R.R. masonary work in 1:4 Cement sand mortar | 1 | 10 | 0.35 | 0.7 | 2.45 | m 3
5 | Cement pointing 1:3 on external and
| Inside wall and Top | 1 | 10 | 1.86 |  | 18.6 | m 2
Component: Access road Construction
S.no. | Description of work | No. | Length | Breadth | Height | Quantity | Unit
1 | E/W in excavation in Boulder mixed soil | 1 | 10 | 3 | 0.6 | 18 | m 3
Component: Pipe Laying and Relaying Work
S.no. | Description of work |  | Length | Breadth | Height | quantity | Unit
1 | E/W in excavation in boulder mixed soil
before treatment plant for extraction of
| existing pipe | 1 | 50 | 0.6 | 0.9 | 27
before and after treatment plant for
| laying of new line | 1 | 50 | 0.6 | 0.9 | 27
|  |  |  | Total |  | 54 | m3
2 | Earthwork refilling in Boulder mixed soil | 1 | 100 | 0.6 | 0.9 | 54 | m3
3 | Laying and Jointing of 140 mm
| dia. HDPE pipe of 10 kg/cm2 |  | 100 |  |  | 100 | r m
Component: Gabion Work for protection
S.no. | Description of work | No. | Length | Breadth | Height | quantity | Unit
1 | Gabion preparation, mesh forming etc.
| (3 m x1 m x 1 m) | 6 |  |  |  | 6 | no.
2 | Filling of Gabion box with stone | 18 |  |  |  | 18 | m3

## QTY.Reservoir_400m3 (hidden)
DETAIL QUANTITY ESTIMATES OF CIRCULAR RCC RESERVOIR 400 m3
Description of Work :- Circular RCC Ground Reservoir (400 cu m)
S.No. | Description of Works | No. | Length | Breadth | Height | Quantity | Remarks
I. | [7 empty] | 13.9
1 | Site Clearance | 1 | 153.938 | Area |  | 153.938
[5 empty] | Total | 153.938 | m2
2 | Earthwork in excavation in foundation | 1 | 153.938 | Area | 1.35 | 207.8164
[5 empty] | Total | 207.8164 | m3
3 | Stone soling | 1 | 151.7468 | Area | 0.2 | 30.3494
[5 empty] | Total | 30.3494 | m3
4 | Plain Cement Concrete P.C.C. (M10) in 1:3:6
| Base | 1 | 151.7468 | Area | 0.15 | 22.762
[5 empty] | Total | 22.762 | m3
5 | Cement Concrete work for R.C.C (1:1.5:3) (M20) for
| Base | 1 | 151.7468 | Area | 0.72 | 109.2577
| Wall L = pi * 11.825m | 1 | 38.4845 | 0.425 | 4.35 | 71.1482
| Ring Beam | 1 | 39.7411 | 0.35 | 0.35 | 4.8683
| Top slab | 1 | 17.3025 | Cu m |  | 17.3025
| Deduction for ventilation | -1 | 0.7854 | Area | 0.15 | -0.11781
| Wall of ventilation | 1 | 3.6128 | 0.15 | 0.42 | 0.22761
|  | 1 | 3.927 | 0.05 | 0.08 | 0.015708
| Ventilation slab cover on top | 1 | 1.0936 | Area | 0.075 | 0.082019
| Deduction for ventilating holes on slab tob | -4 | 0.041548 | Area | 0.15 | -0.024929
[5 empty] | Total | 202.7593 | m3
6 | Reinforcement Bar for RCC |  |  |  |  | 12562 | Kg
7 | Erecting, centering and shuttering of formwork for RCC
| Base edge | 1 | 43.6681 |  | 0.15 | 6.5502
| Tank Base edge | 1 | 43.6681 |  | 0.6 | 26.2009
| Inner Wall | 1 | 35.8142 |  | 4.7 | 168.3265
| Outer Wall | 1 | 39.8982 |  | 4.35 | 173.5573
| Ring Beam | 1 | 39.7411 |  | 0.85 | 33.78
| Top Slab Bottom | 1 | 111.5944 | Area |  | 111.5944
| Ventilation Wall (Inner) | 1 | 3.1416 |  | 0.56 | 1.7593
|  | 1 | 3.7699 |  | 0.08 | 0.30159
| Ventilation Wall (Outer) | 1 | 4.0841 |  | 0.5 | 2.042
| Deduction for ventilation | -1 | 0.7854 | Area |  | -0.7854
| Deduction for ventilating holes on slab tob | -4 | 0.041548 | Area |  | -0.16619
| Top Ventilating Slab | 1 | 0.7854 | Area |  | 0.7854
| Edge of top ventilating slab | 1 | 3.7071 |  | 0.075 | 0.27803
[5 empty] | Total | 524.2241 | m2
8 | 12.5 mm thick outside cement plaster in 1:4 C/M | [7 empty] | 9.9566
| Outer Wall | 1 | 39.8982 |  | 4 | 159.5929
| Ring Beam | 1 | 39.7411 |  | 0.85 | 33.78
| Slab tob | 1 | 124.5711 | Area |  | 124.5711
| Ventilation Wall | 1 | 4.0841 |  | 0.5 | 2.042
| Cover slab | 1 | 1.0936 | Area |  | 1.0936
| Cover slab edge | 1 | 3.7071 |  | 0.075 | 0.27803
| Deduction for ventilation | -1 | 0.7854 | Area |  | -0.7854
| Deduction for ventilating holes on slab tob | -4 | 0.041548 | Area |  | -0.16619
[5 empty] | Total | 320.406 | m2 |  | 0 | 0 | 0
9 | 20 mm thick cement plaster inside tank 1:3 C/M | [7 empty] | 0
| Inner Wall | 1 | 35.8142 |  | 4.7 | 168.3265
| Floor | 1 | 102.0703 | Area |  | 102.0703
[5 empty] | Total | 270.3969 | m2
10 | 12.5 mm thick Cement Sand plaster in 1:4 C/M in Ceiling
| Ceiling | 1 | 111.5944 | Area |  | 111.5944
[5 empty] | Total | 111.5944 | m2
11-a | Providing Crystalline Water Proof Treatment | 1 |  |  |  | 381.9913 | m2
11-b | 3 mm thick Cement Punning | 1 |  |  |  | 270.3969 | m2
12 | Earthwork in backfilling
|  | 1 | 43.6681 | 0.6 | 0.4 | 10.4804
|  | 1 | 43.6681 | 0.1 | 0.2 | 0.87336
[5 empty] | Total | 11.3537 | m3
13 | 250 mm thick Plain G.l. Sheet of 16SW Gas a water-stop supplying and fixing | 1 | 39.2699 |  |  | 39.2699 | m
14 | 32mm día. Gl pipe railings and staircase |  |  |  |  | 48 | m
15 | 2 coat enamel paint in railing & inspection ladders on top of primer |  |  |  |  | 48 | m2
16 | Ventilations of Wooden Frame With Chicken Wire Mesh & Mosquito Mesh |  |  |  |  | 4 | set
16 | Manhole Cover |  |  |  |  | 2 | set
17 | Supply and installation Pipes & Fittings
| 250mm dia DI Pipes | 5 |  |  |  | 5 | m
| 250mm dia Sluice Valve | 1 |  |  |  | 1 | No.
| Mechanical Coupling 250mm dia | 1 |  |  |  | 1 | No.
| 250 Bend 90 | 2 |  |  |  | 2 | No.
II. | Surface Drainage Works
1 | Earthwork in Excavation | 1 | 78.32 | 1.6 | 1.0303 | 129.1102 | Cu m
[5 empty] | Total | 129.1102 | Cu m
2 | Fiat Brick Soiing | 1 | 78.32 | 1 |  | 78.32 | Sq m
[5 empty] | Total | 78.32 | Sq m
3 | M-10 Grade Concreting Work for Lean Concrete (1:3:6) in Foundation | 1 | 78.32 | 1 | 0.075 | 5.874 | Cu m
[5 empty] | Total | 5.874 | Cu m
4 | Formwork
| Base | 1 | 164.86 |  | 0.075 | 12.3645 | Sq m
[5 empty] | Total | 12.3645 | Sq m
5 | Brick Work in 1:4 C/S | 2 | 80 | 0.23 | 0.448 | 16.4864 | Cu m
[5 empty] | Total | 16.4864 | Cu m
6 | 12.5 mm thick cement plaster in 1:4 C/M | 1 | 80.247 | 3.3 |  | 264.8151 | Sq m
7 | Earth Work in Back Filling |  |  |  |  | 124.86 | Cu m
8 | Grass Turfing Around Tank Área | 1 | 75 | 6 |  | 450 | Sq m

## Source (hidden)
Description of Sources
|  |  |  | Discharge | Date | Yield |  | Quality | Dispute | Remarks
S.No. | Name of Source | Location of source | Type of Source | measured | of | Safe | Tapped | (by eye observation) |  | (Specify if land slide upstream settlement, pollution, etc)
|  | Place, VDC-wards |  | Lps | Measurement | Lps | Lps
1 | Kakune Khola | Bame | Stream | 0.88 |  | 0.792 | 0.88 | Good | No | Not any
2 | Bara Khola | Bame | Stream | 0.29 |  | 0.261 | 0.29 | Good | No | Not any
3 |  | Bame | Spring | 0.5 |  | 0.45 | 0.5 | Good | No | Not any

## Pipe-existing (hidden)
Procurement of Pipes
[7 empty] | Rate of HDPE Pipe = | 250
S.No. | Pipe size and series |  | Unit | Quantity | Rate | Amount
[5 empty] | Rs./unit | Rs.
1 | HDPE pipes
Scheme 1
| 32 | 6 | m | 0 | Existing | Existing |  |  | Tr | Dr | Total | DL
| 40 | 6 | m | 0 | Existing | Existing |  | GPM-15 | 0 | 0 | 0 | 0
| 50 | 6 | m | 0 | Existing | Existing |  | GPM-20 | 0 | 0 | 0 | 0
| 63 | 6 | m | 0 | Existing | Existing |  | GPM-25 | 0 | 0 | 0 | 0
| 75 | 6 | m | 0 | Existing | Existing |  | GPM-32 | 0 | 0 | 0 | 0
| 90 | 6 | m | 0 | Existing | Existing |  | GPM-40 | 0 | 0 | 0 | 0
| 110 | 6 | m | 0 | Existing | Existing |  | GPM-50 | 0 | 0 | 0 | 0
| 125 | 6 | m | 0 | Existing | Existing |  | GPM-65 |  |  | 0 | 0
| 16 | 10 | m | 0 | Existing | Existing |  | GPM-80 |  |  | 0 | 0
| 20 | 10 | m | 0 | Existing | Existing |  | GPM-100 |  |  | 0 | 0 | scheme 2
| 25 | 10 | m | 0 | Existing | Existing |  | GPM-125 |  |  | 0 | 0 | scheme 1
| 32 | 10 | m | 0 | Existing | Existing |  | GPM-150 |  |  | 0 | 0
| 40 | 10 | m | 0 | Existing | Existing |  | HP6-32 |  |  | 0 | 0
| 50 | 10 | m | 1565 | Existing | Existing |  | HP6-40 |  |  | 0 | 0
| 63 | 10 | m | 1138 | Existing | Existing |  | HP6-50 |  |  | 0 | 0
| 75 | 10 | m | 2657 | Existing | Existing |  | HP6-63 |  |  | 0 | 0
| 90 | 10 | m | 1362 | Existing | Existing |  | HP6-75 |  |  | 0 | 0 |  | 1379.6
| 110 | 10 | m | 772 | Existing | Existing |  | HP6-90 |  |  | 0 | 0
| 125 | 10 | m | 0 | Existing | Existing |  | HP6-110 |  |  | 0 | 0
| 110 | 4 | m |  | Existing | Existing |  | HP6-125 |  |  | 0 | 0
| 63 | 4 | m |  | Existing | Existing |  | HP10-16 |  |  | 0 | 0
| 250 | 10 | m | 27 | Existing | Existing |  | HP10-20 |  |  | 0 | 0
[8 empty] | HP10-25 |  |  | 0 | 0
|  | Subtotal |  | 7521 | Rs. | 0 |  | HP10-32 |  |  | 0 | 0
| Add transportation cost |  |  |  | 5 | 0 |  | HP10-40 |  |  | 0 | 0
|  | Total |  |  |  | 0 |  | HP10-50 |  | 1422 | 1422 | 1565
| Value added Tax |  |  |  | 13 | 0 |  | HP10-63 |  | 1034 | 1034 | 1138
| Total cost of HDPE pipes |  |  |  | Rs. | 0 |  | HP10-75 | 0 | 2415 | 2415 | 2657
2 | GI pipes | [6 empty] | HP10-90 | 0 | 1238 | 1238 | 1362
| 15 | GI (Heavy) | m | 0 | 203 | 0 |  | HP10-110 | 0 | 701 | 701 | 772
| 25 | GI (Heavy) | m | 0 | 383 | 0 |  | HP10-125 | 0 | 0 | 0 | 0
| 32 | GI (Heavy) | m | 0 | 490 | 0 |  | HP10-140 |  | 0 | 0 | 0
| 40 | GI (Heavy) | m | 0 | 565 | 0 |  | HP10-160 |  | 726 | 726 | 799
| 50 | GI (Heavy) | m | 0 | 823 | 0 |  | HP10-180 |  | 0 | 0 | 0
| 80 | GI (Heavy) | m | 0 | 1215 | 0 |  | HP10-200 |  | 145 | 145 | 160
| 100 | GI (Heavy) | m | 0 | 1883 | 0 |  | HP10-225 |  | 0 | 0 | 0
| 125 | GI (Heavy) | m | 0 | 2440 | 0 |  | HP10-250 |  | 24 | 24 | 27
| 150 | GI (Heavy) | m | 0 | 2767 | 0
| Total cost of GI pipes |  |  | 0 |  | 0
| Add transportation cost |  |  |  | 5 | 0
|  | Total |  |  |  | 0 |  |  |  |  | 7705 | 8480
| Value added Tax |  |  |  | 13 | 0
| Total Cost of GI Pipes With VAT |  |  |  |  | 0
|  | Total cost of HDPE and GI pipes |  | 7521 | Rs. | 0
Detailed Quantities of Pipes & Fittings and Transportation
S.No. | Pipe size and series |  | Unit | Actual length | Unit weight | Total weight ( kg )
Scheme No - 1
1 | HDPE pipes
| 32 | 6 | m | 0 | 0.226 | 0
| 40 | 6 | m | 0 | 0.35 | 0
| 50 | 6 | m | 0 | 0.542 | 0
| 63 | 6 | m | 0 | 0.85 | 0
| 75 | 6 | m | 0 | 1.191 | 0
| 90 | 6 | m | 0 | 1.715 | 0
| 110 | 6 | m | 0 | 2.545 | 0
| 125 | 6 | m | 0 | 3.293 | 0
| 16 | 10 | m | 0 | 0.092 | 0
| 20 | 10 | m | 0 | 0.134 | 0
| 25 | 10 | m | 0 | 0.202 | 0
| 32 | 10 | m | 0 | 0.334 | 0
| 40 | 10 | m | 0 | 0.514 | 0
| 50 | 10 | m | 1565 | 0.796 | 1245.74
| 63 | 10 | m | 1138 | 1.269 | 1444.122
| 75 | 10 | m | 2657 | 1.782 | 4734.774
| 90 | 10 | m | 1362 | 2.568 | 3497.616
| 110 | 10 | m | 772 | 3.801 | 2934.372
| 125 | 10 | m | 0 | 4.962 | 0
| 110 | 4 | m | 0 | 1.703 | 0
| 63 | 4 | m | 0 | 0.585 | 0
| 250 | 10 | m | 27 | 19.757 | 533.439
|  | Subtotal |  | 7521 |  | 14390.063
GI pipes
| 15 | GI (Heavy) | m | 0 | 1.513 | 0
| 25 | GI (Heavy) | m | 0 | 3.077 | 0
| 32 | GI (Heavy) | m | 0 | 3.968 | 0
| 40 | GI (Heavy) | m | 0 | 4.587 | 0
| 50 | GI (Heavy) | m | 0 | 6.369 | 0
| 80 | GI (Heavy) | m | 0 | 10.417 | 0
| 100 | GI (Heavy) | m | 0 | 15.436 | 0
| 125 | GI (Heavy) | m | 0 | 18.52 | 0
| 150 | GI (Heavy) | m | 0 | 22.22 | 0
| Subtotal |  |  | 0 |  | 0
| Weight of fittings and tools |  |  |  |  | 4376.6696
| Total weight of pipe and fittings for transportation |  |  |  |  | 18766.7326

## Pipe (hidden)
Procurement of Pipes
[7 empty] | Rate of HDPE Pipe = | 250
S.No. | Pipe size and series |  | Unit | Quantity | Rate | Amount
[5 empty] | Rs./unit | Rs.
1 | HDPE pipes
Scheme 1
| 32 | 6 | m | 0 | 56.5 | 0 |  |  | Tr | Dr | Total | DL
| 40 | 6 | m | 0 | 87.5 | 0 |  | GPM-15 | 0 | 0 | 0 | 0
| 50 | 6 | m | 0 | 135.5 | 0 |  | GPM-20 | 0 | 0 | 0 | 0
| 63 | 6 | m | 0 | 212.5 | 0 |  | GPM-25 | 0 | 0 | 0 | 0
| 75 | 6 | m | 0 | 297.75 | 0 |  | GPM-32 | 0 | 0 | 0 | 0
| 90 | 6 | m | 0 | 428.75 | 0 |  | GPM-40 | 0 | 0 | 0 | 0
| 110 | 6 | m | 0 | 636.25 | 0 |  | GPM-50 | 0 | 0 | 0 | 0
| 125 | 6 | m | 0 | 823.25 | 0 |  | GPM-65 | 0 | 0 | 0 | 0
| 16 | 10 | m | 0 | 23 | 0 |  | GPM-80 | 0 | 0 | 0 | 0
| 20 | 10 | m | 0 | 33.5 | 0 |  | GPM-100 | 100 | 1976.48 | 2076.48 | 2285 | scheme 2
| 25 | 10 | m | 0 | 50.5 | 0 |  | GPM-125 |  |  | 0 | 0 | scheme 1
| 32 | 10 | m | 0 | 83.5 | 0 |  | GPM-150 | 158.63 | 1231 | 1389.63 | 1529
| 40 | 10 | m | 0 | 128.5 | 0 |  | HP6-32 |  |  | 0 | 0
| 50 | 10 | m | 0 | 199 | 0 |  | HP6-40 |  |  | 0 | 0
| 63 | 10 | m | 0 | 317.25 | 0 |  | HP6-50 |  |  | 0 | 0
| 75 | 10 | m | 0 | 445.5 | 0 |  | HP6-63 |  |  | 0 | 0
| 90 | 10 | m | 0 | 642 | 0 |  | HP6-75 |  |  | 0 | 0 |  | 1379.6
| 110 | 10 | m | 0 | 950.25 | 0 |  | HP6-90 |  |  | 0 | 0
| 125 | 10 | m | 0 | 1240.5 | 0 |  | HP6-110 |  |  | 0 | 0
| 110 | 4 | m |  | 425.75 | 0 |  | HP6-125 |  |  | 0 | 0
| 63 | 4 | m |  | 146.25 | 0 |  | HP10-16 |  |  | 0 | 0
| 250 | 10 | m | 1518 | 4939.25 | 7497781.5 |  | HP10-20 |  |  | 0 | 0
[8 empty] | HP10-25 |  |  | 0 | 0
|  | Subtotal |  | 1518 | Rs. | 7497781.5 |  | HP10-32 |  |  | 0 | 0
| Add transportation cost |  |  |  | 5 | 374889.075 |  | HP10-40 |  |  | 0 | 0
|  | Total |  |  |  | 7872670.575 |  | HP10-50 |  |  | 0 | 0
| Value added Tax |  |  |  | 13 | 1023447.1748 |  | HP10-63 |  |  | 0 | 0
| Total cost of HDPE pipes |  |  |  | Rs. | 8896117.7497 |  | HP10-75 | 0 | 0 | 0 | 0
2 | GI pipes | [6 empty] | HP10-90 | 0 | 0 | 0 | 0
| 15 | GI (Heavy) | m | 0 | 203 | 0 |  | HP10-110 | 0 | 0 | 0 | 0
| 25 | GI (Heavy) | m | 0 | 383 | 0 |  | HP10-125 | 0 | 0 | 0 | 0
| 32 | GI (Heavy) | m | 0 | 490 | 0 |  | HP10-140 |  |  | 0 | 0
| 40 | GI (Heavy) | m | 0 | 565 | 0 |  | HP10-160 |  |  | 0 | 0
| 50 | GI (Heavy) | m | 0 | 823 | 0 |  | HP10-180 |  |  | 0 | 0
| 80 | GI (Heavy) | m | 0 | 1215 | 0 |  | HP10-200 |  |  | 0 | 0
| 100 | GI (Heavy) | m | 2285 | 1883 | 4302655 |  | HP10-225 |  |  | 0 | 0
| 125 | GI (Heavy) | m | 0 | 2440 | 0 |  | HP10-250 |  | 1380 | 1380 | 1518
| 150 | GI (Heavy) | m | 1529 | 2767 | 4230743
| Total cost of GI pipes |  |  | 3814 |  | 8533398
| Add transportation cost |  |  |  | 5 | 426669.9
|  | Total |  |  |  | 8960067.9 |  |  |  |  | 4846.11 | 5332
| Value added Tax |  |  |  | 13 | 1109341.74
| Total Cost of GI Pipes With VAT |  |  |  |  | 10069409.64
|  | Total cost of HDPE and GI pipes |  | 5332 | Rs. | 18965527.3898
Detailed Quantities of Pipes & Fittings and Transportation
S.No. | Pipe size and series |  | Unit | Actual length | Unit weight | Total weight ( kg )
Scheme No - 1
1 | HDPE pipes
| 32 | 6 | m | 0 | 0.226 | 0
| 40 | 6 | m | 0 | 0.35 | 0
| 50 | 6 | m | 0 | 0.542 | 0
| 63 | 6 | m | 0 | 0.85 | 0
| 75 | 6 | m | 0 | 1.191 | 0
| 90 | 6 | m | 0 | 1.715 | 0
| 110 | 6 | m | 0 | 2.545 | 0
| 125 | 6 | m | 0 | 3.293 | 0
| 16 | 10 | m | 0 | 0.092 | 0
| 20 | 10 | m | 0 | 0.134 | 0
| 25 | 10 | m | 0 | 0.202 | 0
| 32 | 10 | m | 0 | 0.334 | 0
| 40 | 10 | m | 0 | 0.514 | 0
| 50 | 10 | m | 0 | 0.796 | 0
| 63 | 10 | m | 0 | 1.269 | 0
| 75 | 10 | m | 0 | 1.782 | 0
| 90 | 10 | m | 0 | 2.568 | 0
| 110 | 10 | m | 0 | 3.801 | 0
| 125 | 10 | m | 0 | 4.962 | 0
| 110 | 4 | m | 0 | 1.703 | 0
| 63 | 4 | m | 0 | 0.585 | 0
| 250 | 10 | m | 1518 | 19.757 | 29991.126
|  | Subtotal |  | 1518 |  | 29991.126
GI pipes
| 15 | GI (Heavy) | m | 0 | 1.513 | 0
| 25 | GI (Heavy) | m | 0 | 3.077 | 0
| 32 | GI (Heavy) | m | 0 | 3.968 | 0
| 40 | GI (Heavy) | m | 0 | 4.587 | 0
| 50 | GI (Heavy) | m | 0 | 6.369 | 0
| 80 | GI (Heavy) | m | 0 | 10.417 | 0
| 100 | GI (Heavy) | m | 2285 | 15.436 | 35271.26
| 125 | GI (Heavy) | m | 0 | 18.52 | 0
| 150 | GI (Heavy) | m | 1529 | 22.22 | 33974.38
| Subtotal |  |  | 3814 |  | 69245.64
| Weight of fittings and tools |  |  |  |  | 17103.675
| Total weight of pipe and fittings for transportation |  |  |  |  | 116340.441

## Qty Truss (hidden)
Details Quantity Estimate Truss
S.N. | Description of Works | Nos. | Length (ft) | Breadth (ft) | Height (ft) | Quantity | Unit | Remark
1 | Site Clearance Work:
|  | 1 |  |  |  | 0 | Job
2 | Earthwork in Excavation:
|  | 9 | 2 | 2 | 2.5 | 90
0
|  |  |  | Total (Cft) |  | 90 | Cft
3 | Earthwork in Backfilling:
|  | 1 | @ 30% of Excavation: |  |  | 27 | Cft
4 | Brick Soling Works
| At Foundation | 9 | 2 | 2 |  | 36
|  |  |  | Total (Sft) |  | 36 | Sft
5 | 3" PCC Work:
| At Foundation | 9 | 2 | 2 |  | 36
0
|  |  |  | Total (Sft) |  | 36 | Sft
6 | PCC for lintel ( 1:1.5:3)
| For Foundation of 4" Pipe | 9 | 1 | 1 | 0.5 | 4.5
| Total |  |  |  |  | 4.5 | Cft
7 | Brick Work:
| Below DPC: 1st step | 9 | 4 | CSA | 1 | 36
| 2nd and 3rd step | 9 | 2.5 | CSA | 1 | 22.5
|  |  |  | Total (Cft): |  | 58.5 | Cft
8 | Black Iron Pipe Truss Work:
| 4'' Iron Post | 9 | 11.75 | 6.01 | Kg/m | 193.7675
| 2" Base Tie | 3 | 11.5 | 2.3 | Kg/m | 24.1921
| 2" Rafter | 6 | 7 | 2.3 | Kg/m | 29.4512
| 1.5" Purlins: | 6 | 15 | 1.72 | Kg/m | 47.1951
| 1.5" Struts: | 12 | 40 | 1.72 | Kg/m | 251.7073
|  |  |  | Total (Kg): |  | 546.3133 | Kg
9 | Coloured CGI Roofing Work:
|  | 2 | 18.4 | 13.2 |  | 485.76
|  |  |  | Total (Sft): |  | 485.76 | Sft
16 | Ridge Work: | 1 | 18.4 |  |  | 18.4
|  |  |  | Total (Rft): |  | 18.4 | Rft
10 | Gutter Work: | 2 | 18.4 |  |  | 36.8
|  |  |  | Total (Rft): |  | 36.8 | Rft

## pip-line (hidden)
Abstract of costs | [8 empty] | 1.4811
Pipeline Works | [9 empty] | 250
(per kg)
Sn | Description | Length | Breadth | Height | Quantity | Unit | Rate | Amount
A | Transmission line
1 | E/W in excavation in hard soil | 284.493 | 0.45 | 0.9 | 115.22 | m3 | 1362.18 | 156950.38 |  |  | Tr | Dr | Tr | Dr | Total | DL
2 | E/W in backfilling with hard soil | 284.493 | 0.45 | 0.9 | 115.22 | m3 | 686.54 | 79103.14 |  | GPM-15 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | GPM-20 | 0 | 0 | 0 | 0 | 0 | 0
3 | Laying & Jointing of Pipes | [8 empty] | GPM-25 | 0 | 0 | 0 | 0 | 0 | 0
| 32 mmØ HDPE pipe | 0 |  |  | 0 | m | 6.02 | 0 |  | GPM-32 | 0 | 0 | 0 | 0 | 0 | 0
| 40,50 mmØ HDPE pipe | 0 |  |  | 0 | m | 7.32 | 0 |  | GPM-40 | 0 | 0 | 0 | 0 | 0 | 0
| 63-90 mmØ HDPE | 0 |  |  | 0 | m | 96.87 | 0 |  | GPM-50 | 0 | 0 | 0 | 0 | 0 | 0
| 25,32 mmØ GI pipe | 0 |  |  | 0 | m | 145.44 | 0 |  | GPM-65 | 0 | 0 | 0 | 0 | 0 | 0
| 40,50 mmØ GI pipe | 0 |  |  | 0 | m | 198.32 | 0 |  | GPM-80 | 0 | 0 | 0 | 0 | 0 | 0
| 65,80 mmØ GI pipe | 0 |  |  | 0 | m | 264.41 | 0 |  | GPM-100 | 100 | 1976.48 | 110 | 2174.128 | 2076.48 | 2284.128
| 100 mmØ GI pipe | 110 |  |  | 110 | m | 330.5 | 36355 |  | GPM-125 | 0 | 0 | 0 | 0 | 0 | 0
| 125 mmØ GI pipe | 0 |  |  | 0 | m | 403.22 | 0 |  | GPM-150 | 158.63 | 1231 | 174.493 | 1354.1 | 1389.63 | 1528.593
| 150 mmØ GI pipe | 175 |  |  | 175 | m | 462.73 | 80977.75 |  | HP6-32 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | HP6-40 | 0 | 0 | 0 | 0 | 0 | 0
| Sub-total | 285 |  |  | 285 |  |  | 353386.27 |  | HP6-50 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | [6 empty] | 45940.2151 |  | HP6-63 | 0 | 0 | 0 | 0 | 0 | 0
| Total cost of transmission pipe line works | [5 empty] | Rs. | 399326.4851 |  | HP6-75 | 0 | 0 | 0 | 0 | 0 | 0
B | Distribution line | [8 empty] | HP6-90 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | HP6-110 | 0 | 0 | 0 | 0 | 0 | 0
1 | E/W in excavation in hard soil | 3528.228 | 0.45 | 0.9 | 1428.93 | m³ | 1362.18 | 1946459.87 |  | HP6-125 | 0 | 0 | 0 | 0 | 0 | 0
2 | E/W in backfilling with hard soil | 3528.228 | 0.45 | 0.9 | 1428.93 | m³ | 686.54 | 981017.6 |  | HP10-16 | 0 | 0 | 0 | 0 | 0 | 0
3 | Laying & Jointing of Pipes | [8 empty] | HP10-20 | 0 | 0 | 0 | 0 | 0 | 0
| 16 mmØ HDPE pipe | 0 |  |  | 0 | m | 0 | 0 |  | HP10-25 | 0 | 0 | 0 | 0 | 0 | 0
| 20,25 mmØ HDPE pipe | 0 |  |  | 0 | m | 4.88 | 0 |  | HP10-32 | 0 | 0 | 0 | 0 | 0 | 0
| 32 mmØ HDPE pipe | 0 |  |  | 0 | m | 6.02 | 0 |  | HP10-40 | 0 | 0 | 0 | 0 | 0 | 0
| 40, 50 mmØ HDPE pipe | 0 |  |  | 0 | m | 7.32 | 0 |  | HP10-50 | 0 | 0 | 0 | 0 | 0 | 0
| 63-90 mmØ HDPE | 0 |  |  | 0 | m | 96.87 | 0 |  | HP10-63 | 0 | 0 | 0 | 0 | 0 | 0
| 110,125 mmØ HDPE pipe | 0 |  |  | 0 | m | 142.69 | 0 |  | HP10-75 | 0 | 0 | 0 | 0 | 0 | 0
| 250 mmØ HDPE pipe | 1518 |  |  | 1518 | m | 272.27 | 413305.86 |  | HP10-90 | 0 | 0 | 0 | 0 | 0 | 0
| 15,20 mmØ GI pipe | 0 |  |  | 0 | m | 105.76 | 0 |  | HP10-110 | 0 | 0 | 0 | 0 | 0 | 0
| 25,32 mmØ GI pipe | 0 |  |  | 0 | m | 145.44 | 0 |  | HP10-125 | 0 | 0 | 0 | 0 | 0 | 0
| 40,50 mmØ GI pipe | 0 |  |  | 0 | m | 198.32 | 0
| 65,80 mmØ GI pipe | 0 |  |  | 0 | m | 264.41 | 0 |  | HP10-180 | 0 | 0 | 0 | 0 | 0 | 0
| 100 mmØ GI pipe | 2175 |  |  | 2175 | m | 330.5 | 718837.5 |  | HP10-200 | 0 | 0 | 0 | 0 | 0 | 0
| 125 mmØ GI pipe | 0 |  |  | 0 | m | 403.22 | 0 |  | HP10-225 | 0 | 0 | 0 | 0 | 0 | 0
| 150 mmØ GI pipe | 1355 |  |  | 1355 | m | 462.73 | 626999.15 |  | HP10-250 | 0 | 1380 | 0 | 1518 | 1380 | 1518
[11 empty] | 258.63 | 3207.48 | 284.493 | 3528.228 | 4846.11 | 5330.721
| Sub-total | 5048 |  |  | 5048 |  | Rs. | 4686619.98
| 13 | [6 empty] | 609260.5974
| Total cost of distribution pipeline works | [5 empty] | Rs. | 5295880.5774
Transportation Cost of Pipes and fittings | Total cost of pipeline works | [5 empty] | Rs. | 5695207.0625
S.No.
1
| Description of items |  |  |  | Quantity | Unit | Rate | Amount
Transportation Cost of Pipes and fittings from store to site
| Total |  |  |  | 116340.441 | kg | 3.463 | 402886.9472
| Sub Total |  |  |  | 116340.441 | kg |  | 402886.9472
| 13 | [6 empty] | 52375.3031
| Total transportation cost | [5 empty] | Rs | 455262.2503

## bar+gate (hidden)
Barbed Wire Fencing & Gate
Sankhu Drinking Water Supply Project
Barbed Wire Fencing ( Type - A)
|  | Total length of fencing = | 24 | m
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rate | Amount
1 | Earthwork in excavation
|  | 17 | 0.35 | 0.35 | 0.6 | 1.25 | m³ | 1362.18 | 1702.73
2 | PCC (1:2:4) for anchor blocks | 17 | 0.35 | 0.35 | 0.6 | 1.25 | m³ | 15694.9 | 19618.63
3 | MS angle post(40*40*6mm size and 2.1m long) | 17 | 2.1 | 3.5 |  | 124.95 | kg | 106.95 | 13363.4
4 | Barbed wire fencing
| - horizontal ( 7 layers) | 7 | 24 |  |  | 168
| - Diagonals | 32 | 1.8196 |  |  | 58.23
| Total |  |  |  |  | 226.23 | m | 99.291 | 22462.6
5 | Enamel painting on MS angle | 17 | 1.5 | 0.16 |  | 4.08 | m² | 378.44 | 1544.04
| Total Amount ( Without VAT ) | [6 empty] | Rs. | 58691.4
| Rate per metre ( Without VAT ) | [6 empty] | Rs. | 2445.48
Entrance Gate
For barbed wire fencing Type-A
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rates | Amount
1 | Earthwork in excavation in foundation
|  | 2 | 0.45 | 0.45 | 0.6 | 0.243 | m³ | 1362.18 | 331.01
2 | Stone soling | 2 | 0.45 | 0.45 | 0.15 | 0.06075 | m³ | 5141.87 | 312.37
3 | Stone masonry in 1:6 c-s mortar | for support pillars
| In foundation | 2 | 0.45 | 0.45 | 0.45 | 0.18225
| Above Ground | 2 | 0.45 | 0.45 | 1.6 | 0.648
| Deduct for holdfast PCC blocks | 3 | 0.45 | 0.45 | 0.2 | -0.12
| Total |  |  |  |  | 0.71025 | m³ | 14084.92 | 10003.81
4 | PCC (1:2:4) for holdfast blocks | 3 | 0.45 | 0.45 | 0.2 | 0.1215
| on top of pillar | 2 | 0.45 | 0.45 | 0.1 | 0.0405
| Total |  |  |  |  | 0.162 | m³ | 15694.9 | 2542.57
5 | 12.5mm 1:4 c - s plaster -Pillars | 8 | 0.45 | - | 1.6 | 5.76
| -On top | 2 | 0.45 | 0.45 | - | 0.405
| Total |  |  |  |  | 6.165 | m² | 478.27 | 2948.53
6 | Mild Steel angle ( 25 x 25 x 3 mm Size ) framed gate with Iron Grill shutter (0.95 x 1.5 m size) all complete including fixing |  |  |  |  | 1 | no | 1725 | 1725
7 | Enamel Painting | 1 | 0.95 | - | 1.5 | 1.425 | m² | 378.44 | 539.28
| Total Amount ( Without VAT ) | [6 empty] | Rs. | 18402.57
Barbed Wire Fencing ( Type - B )
Sankhu Drinking Water Supply Project
|  | Total length of fencing = | 24 | m
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rates | Amount
1 | Earthwork in excavation in HS
|  | 12 | 0.3 | 0.3 | 0.6 | 0.648 | m³ | 1362.18 | 882.69
2 | Dry stone soling | 12 | 0.3 | 0.3 | 0.1 | 0.108 | m³ | 5141.87 | 555.32
2 | PCC (1:3:6) | 12 | 0.2 | 0.2 | 0.5 | 0.24
| - deduction for RCC post | 12 | 0.1 | 0.1 | 0.5 | -0.06
| Net PCC |  |  |  |  | 0.18 | m³ | 14330.41 | 2579.47
3 | Barbed wire fencing on pre-cast RCC post
| - Barbed wire fencing - 5 horizontals | 5 | 24 |  |  | 120
| - diagonals | 24 | 2.4 |  |  | 57.6
| Total |  |  |  |  | 177.6 | m | 99.291 | 17634.08
4 | PCC (1:2:4) for RCC posts | 12 | 2.1 | 0.1 | 0.1 | 0.252 | m³ | 15694.9 | 3955.11
5 | - Mild steel reinforcement
| 10 mm ø bar, 4 nos 2.2 m long | 48 | 2.2 | 0.616 | kg/m | 65.0496
| - Stirrup - 6 mm ø bar, 240 mm long | 132 | 0.24 | 0.22 | kg/m | 6.9696
- Anchor hooks - 6 mm ø bar bent into shape to held barbed wire
|  | 60 | 0.2 | 0.22 | kg/m | 2.64
[6 empty] | 74.6592 | kg | 123.56 | 9224.89
6 | Centering and shuttering | 12 | 0.3 |  | 2.3 | 8.28 | m² | 1278.27 | 10584.08
| Total Amount ( Without VAT ) | [6 empty] | Rs. | 45415.64
| Rate per metre ( Without VAT ) | [6 empty] | Rs. | 1892.32
Entrance Gate
For barbed wire fencing Type-B
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rates | Amount
1 | Earth work in excavation in hard soil
|  | 2 | 0.1 | 0.1 | 0.6 | 0.012 | m³ | 1362.18 | 16.35
2 | Boulder soling | 2 | 0.1 | 0.1 | 0.1 | 0.002 | m³ | 5141.87 | 10.28
3 | Wooden work for post & style
| Wooden post, 100 x 100mm | 2 | 1.9 | 0.1 | 0.1 | 0.038
| Door Style, 75 x 20mm | 2 | 1.3 | 0.075 | 0.02 | 0.0039
| Top, Bottom, 75 x 20mm | 2 | 1 | 0.075 | 0.02 | 0.003
| Diagonal Bracing 75 x 20mm | 1 | 1.64 | 0.075 | 0.02 | 0.00246
| Total |  |  |  |  | 0.04736 | m³ | 326279.6 | 15452.6
4 | Barbed wire 1 m long each | 4 |  |  |  | 4 | m | 99.291 | 397.16
5 | U - hooks | 10 |  |  |  | 10 | no. | 19.69 | 196.9
6 | Locking set |  |  |  |  | 1 | no | 318.55 | 318.55
| Total Amount ( Without VAT ) | [6 empty] | Rs. | 16391.84

## CC-DC (hidden)
Collection Chamber
Sankhu Drinking Water Supply Project
| Inner size of chamber = | 2 | x | 1 |  | Total height = | 2.5
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rate | Amount
1 | Site clearance |  | 3 | 2 |  | 6 | m² | 137.54 | 825.24
2 | Earthwork in excavation for fondation work in hard soil
|  | 1 | 2.9 | 1.9 | 2.5 | 13.775 | m³ | 1362.18 | 18764.03
3 | Dry stone soling | 1 | 2.9 | 1.9 | 0.15 | 0.8265 | m³ | 5141.87 | 4249.76
4 | Plain Cement Concrete (1:2:4)
| in foundation | 1 | 2.9 | 1.9 | 0.1 | 0.551
| Pipe embeddment block | 5 | 0.45 | 0.2 | 0.2 | 0.09
| top of baffle wall | 1 | 1 | 0.35 | 0.1 | 0.035
| Cover slab | 1 | 2.9 | 1.9 | 0.1 | 0.551
Deduct:
| -Manhole cover | 2 | 0.6 | 0.6 | 0.05 | -0.036
| Total |  |  |  |  | 1.191 | m³ | 15694.9 | 18692.63
5 | Stone masonry work in 1:4 c-s mortar
| CC portion | 1 | 7.8 | 0.45 | 2.5 | 8.775
| baffle wall | 1 | 1 | 0.35 | 0.6 | 0.21
| Deduct - for PCC blocks | 5 | 0.45 | 0.2 | 0.2 | -0.09
| Total |  |  |  |  | 8.895 | m³ | 14865.17 | 132225.69
6 | Centering & shuttering work for PCC/RCC
| Bottom of cover slab - CC portion | 1 | 1.65 | 1 |  | 1.65
| -Outer edge of cover slab | 1 | 9.6 | - | 0.1 | 0.96
| Total form work |  |  |  |  | 2.61 | m² | 1278.27 | 3336.28
7 | Steel reinforcement
| 8 mm ø @ 150 mm c/c bothways | 12 | 1.9 | 0.395 |  | 9.006
|  | 14 | 1.7 | 0.395 |  | 9.401
| Total reinforcement |  |  |  |  | 18.407 | kg | 123.56 | 2274.37
8 | 12.5 mm thick 1:4 c-s plaster
| floor of CC | 1 | 1.65 | 1 |  | 1.65
| Inner sides of Walls of CC | 2 | 1.65 | - | 2.5 | 8.25
|  | 2 | 1 | - | 2.5 | 5
| Side of baffle wall | 2 | 1 |  | 0.7 | 1.4
| top of baffle wall | 1 | 1 | 0.35 |  | 0.35
| Outer portion of all walls above GL | 1 | 9.6 | - | 0.3 | 2.88
| Total |  |  |  |  | 19.53 | m² | 478.27 | 9340.61
9 | 3 mm thick 1:1 c-s punning
|  | as per plaster |  |  |  | 19.53
| Deduct for outer portion |  |  |  |  | -2.88
| Total |  |  |  |  | 16.65 | m² | 332.33 | 5533.29
10 | Supply and installation of standard man hole cover - 600×600 mm² | 2 |  |  |  | 2 | set | 2452.95 | 4905.9
11 | Installation of pipes and fittings |  |  |  |  | 1 | job | 500 | 500
| Subtotal | [7 empty] | 200647.8
| Add Value Added Tax | [6 empty] | 13 | 26084.214
| Total Amount | [7 empty] | 226732.014
Distribution Chamber
| Inner size of CC portion: | 2 | x | 0.8 | Total height |  | 1
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rate | Amount
1 | Site clearance |  | 3 | 2 |  | 6 | m² | 137.54 | 825.24
2 | Earthwork in excavation for fondation work in hard soil
|  | 1 | 2.9 | 1.7 | 1 | 4.93 | m³ | 1362.18 | 6715.55
3 | Dry stone soling | 1 | 2.9 | 1.7 | 0.15 | 0.7395 | m³ | 5141.87 | 3802.41
4 | Plain Cement Concrete (1:2:4)
| in foundation | 1 | 2.9 | 1.7 | 0.1 | 0.493
| Pipe embeddment block | 6 | 0.45 | 0.2 | 0.2 | 0.108
| Cover slab | 1 | 2.9 | 1.7 | 0.08 | 0.3944
Deduct:
| -Manhole cover | 2 | 0.6 | 0.6 | 0.05 | -0.1131
| Total |  |  |  |  | 0.8823 | m³ | 15694.9 | 13847.65
5 | Stone masonry work in 1:4 c-s mortar
| CC portion | 1 | 7.4 | 0.45 | 1 | 3.33
| Partition wall | 1 | 0.8 | 0.35 | 1 | 0.28
| Total |  |  |  |  | 3.61 | m³ | 14865.17 | 53663.26
6 | Centering & shuttering work for PCC/RCC
| Bottom of cover slab - CC portion | 1 | 1.65 | 0.8 |  | 1.32
| -Outer edge of cover slab | 1 | 9.2 | - | 0.08 | 0.74
| Total form work |  |  |  |  | 2.06 | m² | 1278.27 | 2633.24
7 | Steel reinforcement
| 8 mm ø @ 175 mm c/c bothways | 18 | 1.7 | 0.395 |  | 12.087
|  | 12 | 2.9 | 0.395 |  | 13.746
| Deduct for man hole | 16 | 0.6 | 0.395 |  | -3.792
| Net reinforcement |  |  |  |  | 22.041 | kg | 123.56 | 2723.39
8 | 12.5 mm thick 1:4 c-s plaster
| floor of CC | 1 | 1.65 | 0.8 |  | 1.32
| Inner sides of Walls of CC | 2 | 1.65 | - | 1 | 3.3
|  | 2 | 0.8 | - | 1 | 1.6
| Side of partition wall | 2 | 0.8 |  | 1 | 1.6
| Outer Portion of all walls above GL | 1 | 9.2 | - | 0.3 | 2.76
| Total |  |  |  |  | 10.58 | m² | 478.27 | 5060.1
9 | 3 mm thick 1:1 c-s punning
|  | as per plaster |  |  |  | 10.58
| Deduct for outer portion |  |  |  |  | -2.76
| Total |  |  |  |  | 7.82 | m² | 332.33 | 2598.82
10 | Supply and installation of standard man hole cover - 600×600 mm² | 2 |  |  |  | 2 | set | 2879.55 | 5759.1
11 | Installation of pipes and fittings |  |  |  |  | 1 | job | 800 | 800
| Subtotal | [7 empty] | 98428.76
| Add Value Added Tax | [6 empty] | 13 | 12795.7388
| Total Amount | [7 empty] | 111224.4988

## Private_Con (hidden)
Quantity Estimate
House Connections
Total nos. of connections |  | 133
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rates | Amount
A | Earth works for pipe laying
1 | E/W in excavation in hard soil | 133 | 15 | 0.4 | 0.5 | 399 | m³ | 1362.18 | 543509.82
2 | E/W in backfilling in hard soil | 133 | 15 | 0.4 | 0.5 | 399 | m³ | 686.54 | 273929.46
| Sub Total | [7 empty] | 817439.28
Quantity of Pipe and fittings
1 | GI pipe 1/2" | 133 | 10 |  |  | 1330 | m | 172 | 228760
2 | Water Meter | 133 | 1 |  |  | 133 | no | 1500 | 199500
3 | Elbow 1/2" | 133 | 3 |  |  | 399 | no | 86 | 34314
4 | Socket 1/2" | 133 | 2 |  |  | 266 | no | 30 | 7980
5 | Nipple 1/2" | 133 | 3 |  |  | 399 | no | 38 | 15162
6 | Ferrule 1/2" | 133 | 1 |  |  | 133 | no | 664 | 88312
7 | Union 1/2" | 133 | 1 |  |  | 133 | no | 118 | 15694
8 | Brass bib cock 1/2" | 133 | 1 |  |  | 133 | no | 400 | 53200
| Sub Total | [7 empty] | 642922
| Total | [7 empty] | 1460361.28
| VAT @ 13% | [7 empty] | 189846.9664
| Total With Vat | [7 empty] | 1650208.2464
| Rate Per HH Connection | [7 empty] | 12407.5808

## Qty_in_1 (hidden)
QUANTITY ESTIMATE
TYPE OF WORK : Intake-3 Construction works-Fedi
S.no. | Description of works | Unit | No. | Length,m | Breadth,m | Height,m | Quantity | Remarks
1 | Site Clearance | sqm | 1 | 8 | 21.3 |  | 170.4
2 | Earthwork Excavation
| RCC Weir | Cum | 1 | 5 | 0.3 | 1.525 | 2.29 |  | 1.75 | 0.56
|  | Cum | 1 | 5 | 1.7 | 0.525 | 4.46
|  | Cum | 1 | 5 | 0.3 | 1.525 | 2.29
|  | Cum | 1 | 5 | 3 | 0.525 | 7.88
| Collection and Valve Chamber | Cum | 1 | 2.1 | 4.05 | 1.8 | 15.31
|  | Cum |  |  |  | Total | 32.23
3 | Stone Soling
| RCC Weir | Cum | 1 | 5 | 5.3 | 0.15 | 3.98
|  |  | 1 | 7.3 | 1.3 | 0.15 | 1.42
| Collection and Valve Chamber | Cum | 1 | 2.1 | 4.85 | 0.15 | 1.53
|  | Cum |  |  |  | Total | 6.93
4.1 | PCC M10
| RCC Weir | Cum | 1 | 5 | 5.3 | 0.075 | 1.99
|  | Cum | 1 | 7.3 | 1.3 | 0.075 | 0.71
| Collection and Valve Chamber | Cum | 1 | 2.1 | 4.85 | 0.075 | 0.76
|  | Cum |  |  |  | Total | 3.46
4.2 | RCC works M20
| RCC Weir Wall | cum | 1 | 5 | 0.3 | 1.525 | 2.29
|  | cum | 1 | 5 | 1.7 | 0.3 | 2.55
|  | cum | 1 | 5 | 0.3 | 2.295 | 3.44
|  | cum | 1 | 5 | 3 | 0.3 | 4.5
| Collection Chamber | cum | 1 | 2.1 | 4.85 | 0.3 | 3.06
| Wall | cum | 1 | 8.3 | 0.3 | 2.15 | 5.35
| Cover slab | cum | 1 | 2.1 | 3.1 | 0.15 | 0.98
Valve Chamber
| Wall | cum | 1 | 4.6 | 0.25 | 2.15 | 2.47
| Cover slab | cum | 1 | 2.1 | 1.25 | 0.15 | 0.39
| Deduction of Manhole Cover | cum | -2 | 0.2826 |  | 0.15 | -0.08
|  | Cum |  |  |  | Total | 24.95
5 | One layer of Water Proofing
| Collection Chamber | sqm | 1 | 2.1 | 4.85 |  | 10.19
| Wall | sqm | 1 | 13.9 |  | 2.15 | 29.89
|  | sqm |  |  |  | Total | 40.08
6 | Form Works
| RCC Weir Base | sqm | 1 | 20.6 |  | 0.075 | 1.55
| RCC Weir Wall | sqm | 1 | 10.6 |  | 1.525 | 16.17
|  | sqm | 1 | 13.4 |  | 0.3 | 4.02
|  | sqm | 1 | 10.6 |  | 2.295 | 24.33
|  | sqm | 1 | 11 |  | 0.3 | 3.3
| Collection Chamber | sqm | 2 | 13.9 |  | 0.3 | 8.34
| Wall | sqm | 1 | 17.2 |  | 2.15 | 36.98
| Cover slab | sqm | 1 | 2.4 | 3.4 |  | 8.16
Valve Chamber
| Wall | sqm | 2 | 4.6 |  | 2.15 | 19.78
| Cover slab | sqm | 1 | 2.4 | 1.55 |  | 3.72
| Deduction of Manhole Cover | sqm | -2 | 0.2826 |  |  | -0.57
|  | sqm |  |  |  | Total | 125.78
7 | Reinforcement | kg |  |  |  |  | 3965.553
9 | 20 to 25mm thick screeding (1:4) on floors
| Collection Chamber | sqm | 1 | 2.5 | 1.5 |  | 3.75
| Valve Chamber | sqm | 1 | 1.5 | 1 |  | 1.5
|  | sqm |  |  |  | Total | 5.25
10 | Cement punning
| Collection Chamber | sqm | 1 | 2.5 | 1.5 |  | 3.75
| Wall | sqm | 2 | 8 |  | 2.15 | 34.4
| Valve Chamber | sqm | 1 | 1.5 | 1 |  | 1.5
| Wall | sqm | 2 | 5 |  | 2.15 | 21.5
|  | sqm |  |  |  | Total | 61.15
11 | 12.5 mm thick cement plaster on concrete surface with 1:3 cement sand mortar
Collection Chamber
| Wall | sqm | 2 | 8 |  | 2.15 | 34.4
| Cover slab | sqm | 2 | 2.4 | 3.4 |  | 16.32
Valve Chamber
| Wall | sqm | 2 | 5 |  | 2.15 | 21.5
| Cover slab | sqm | 2 | 2.4 | 1.55 |  | 7.44
| Deduction of Manhole Cover | sqm | -2 | 0.2826 |  |  | -0.57
|  | sqm |  |  |  | Total | 79.09
12 | Gabion Works
Gabion Rip Rap Mesh
| 2mx1mx0.3m | Cum | 1 | 14 | 10.6 | 0.3 | 44.52
13 | 600dia. Manhole Cover | No. | 2 |  |  |  | 2
15 | Supplying and laying Pipes Fittings
| 75∅ Tee | No. | 2 |  |  |  | 2
| 75∅ Elbow | No. | 2 |  |  |  | 2
| 75∅ Pipe Piece | No. | 10 |  |  |  | 10
| 65∅ Gate Valve | No. | 2 |  |  |  | 2
| 65∅ Union | No. | 2 |  |  |  | 2
| 65∅ Nipple | No. | 2 |  |  |  | 2
| 65/75 GI/PE Flanged set | No. | 2 |  |  |  | 2
| 75∅ PE Stainer | No. | 1 |  |  |  | 1
TYPE OF WORK : Boulder Pitching in river
S.no. | Description of works | Unit | No. | Length,m | Breadth,m | Height,m | Quantity | Remarks
1 | Earthwork Excavation
|  | cum | 1 | 50 | 2.68 | 1 | 134
|  | cum |  |  |  |  | 134
2 | Back filling
|  | cum | 1 | 25 | 1.2 | 1 | 30
|  | cum |  |  |  |  | 30
4 | Masonary Works
4.1 | Stone Soling | cum | 1 | 50 | 1.68 | 0.2 | 16.8
|  | cum |  |  |  |  | 16.8
4.3 | Stone Masonary(1:6)
|  | cum | 1 | 50 | 0.35 | 0.32 | 5.6 |  | 2.1335 | 4.9215
| Gate Pillar | cum | 2 | 0.45 | 0.45 | 1.5 | 0.61
|  | cum |  |  |  |  | 6.21
5 | P.C.C Works
M10
|  | cum | 1 | 50 | 1.68 | 0.1 | 8.4
| In MS Posts Casting (Bottom) | cum | 28 | 0.13 | 0.13 | 0.05 | 0.02
| In MS Posts Casting (Side) | cum | 28 | 0.13 | 0.035 | 0.26 | 0.03
|  | cum |  |  |  |  | 8.45
M15
| Wall Coping | cum | 1 | 50 | 0.35 | 0.05 | 0.88
|  | cum |  |  |  |  | 0.88
6 | Formworks
|  | sqm | 2 | 51.68 |  | 0.1 | 10.34
| Wall Coping | sqm | 2 | 50.35 |  | 0.05 | 5.04
|  | sqm |  |  |  |  | 15.38
7 | 12.5mm thick c/s plaster (1:4) in wall (both sides) and 100mm below GL
|  | sqm | 2 | 0.13 |  | 0.495 | 0.13
|  | sqm |  |  |  |  | 0.13
8 | Fencing by galvanised chain link of 10SWG with 50mm bore MS pipe (@2m c/c), 25x25x4 mm MS angle & 100 mm long 3x20mm MS strip
|  | sqm | 1 | 0.13 |  | 1.78 | 0.23
|  | sqm |  |  |  |  | 0.23
9 | Gabion Works
| 2x1x1 | cum | 16 | 2 | 1 | 1 | 32
|  | cum |  |  |  |  | 32

## int (hidden)
Stream Intake ( Type II )
(Without valve chamber )
| Total length of wing walls | 4 | m | Size of C.C |  | 1 | x | 1
| Height of structure | 1.5 | m
Sankhu Drinking Water Supply Project | [8 empty] | Intake: Damai Kholsi
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rate | Amount
1 | Site Clearance |  | 5 | 3 |  | 15 | m2 | 137.54 | 2063.1
2 | Earthwork in excavation in foundation
| wing wall |  | 4.45 | 0.45 | 1 | 2
| Catchment portion |  | 1.9 | 1.9 | 0.8 | 2.89
| Pipe trench for washout |  | 10 | 0.45 | 1 | 4.5
| water diversion and drainage ditch |  | 10 | 0.5 | 0.5 | 2.5
| Total earth work |  |  |  |  | 11.89 | m³ | 1362.18 | 16196.32
3 | Plain Cement Concrete (1:2:4)
| Wing Walls |  | 4.45 | 0.45 | 0.1 | 0.2
| Catchment Portion |  | 1.9 | 1.9 | 0.1 | 0.361
| At the top of Wing Wall |  | 4.45 | 0.45 | 0.05 | 0.1
| Lintel over drywall |  | 0.7 | 0.45 | 0.1 | 0.032
| Pipe Embeddment blocks | 3 | 0.45 | 0.2 | 0.2 | 0.054
| For cover slab |  | 1.9 | 1.9 | 0.1 | 0.361
Deduct :
| Manhole Cover | 1 | 0.6 | 0.6 | 0.05 | -0.018
| Total |  |  |  |  | 1.09 | m³ | 15694.9 | 17107.44
4 | Stone masonry in 1:4 c-s mortar
| Wing Wall |  | 4.45 | 0.45 | 1.5 | 3
| Walls of CC |  | 5.8 | 0.45 | 1.5 | 3.92
Deduction
| for embeddment block | 3 | 0.45 | 0.2 | 0.2 | -0.05
| for dry wall |  | 0.5 | 0.45 | 0.3 | -0.07
| Total masonry work |  |  |  |  | 6.8 | m³ | 14865.17 | 101083.16
5 | Dry stone masonry |  | 0.5 | 0.45 | 0.3 | 0.07 | m³ | 6783.38 | 474.84
6 | Steel reinforcement
8mm f bars @ 150c/c both ways
| for cover slab | 14 | 1.95 | 0.395 |  | 10.78
|  | 14 | 1.95 | 0.395 |  | 10.78
| Deduction for Manhole Opening | 8 | 0.6 | 0.395 |  | -1.896
| Total |  |  |  |  | 19.664 | kg | 123.56 | 2429.68
7 | Centering & shuttering works for RCC/PCC
| edge of slab | 2 | 1.9 | - | 0.1 | 0.38
|  | 2 | 0.64 | - | 0.1 | 0.13
| Slab Cover - of CC |  | 1 | 1 | - | 1
| Top of wing wall | 2 | 4.45 | - | 0.05 | 0.45
| Total |  |  |  |  | 1.96 | m² | 1278.27 | 2505.41
8 | 12.5 mm thick 1:3 cement sand plaster
| inside of wing walls |  | 5.9 | - | 1.5 | 8.85 | m²
| Inside of CC walls |  | 4 |  | 1.5 | 6
| Floor of CC |  | 1 | 1 | - | 1
| Outside of CC |  | 5.7 |  | 1.6 | 9.12
| Total plastering work |  |  |  |  | 24.97 | m² | 485.7 | 12127.93
9 | 3 mm 1:1cement sand punnig | as plastering work |  |  |  | 24.97
| Deduct for outside of walls |  | 5.7 |  | 1.6 | -9.12
| Total punning work |  |  |  |  | 15.85 | m² | 332.33 | 5267.43
10 | Boulder packing | 1 | 2.76 | 0.6 | 0.5 | 0.828 | m³ | 5141.87 | 4257.47
11 | Standard manhole over 60cm×60cm size |  |  |  |  | 1 | set | 2452.95 | 2452.95
12 | Barbed wire fencing (Type - B) |  |  |  |  | 22 | m | 1892.32 | 41631.04
13 | Wooden entrance gate (1 m x 1.5 m) |  |  |  |  | 1 | no | 16391.84 | 16391.84
14 | Dewatering |  |  |  |  | 1 | Job | 450 | 450
15 | Installation of Pipes & Fittings |  |  |  |  | 1 | job | 600 | 600
| Subtotal | [7 empty] | 225038.61
| Add Value Added Tax | [6 empty] | 13 | 29255.0193
| Total Amount with VAT | [6 empty] | Rs. | 254293.6293

## fe-tank (hidden)
Ferrocement Storage Tank
Sankhu Drinking Water Supply Project |  | 10
| Diameter, d = | 3 | m |  |  | Tank wall height, h = | 1.65 | m
| Dome height, = | 0.5 | m |  | For Scheme # no: | 1 |  |  |  | 345929.7039
S.N. | Description | No. | Radius | Length/Radius | Breadth | Height | Qty. | Unit | Rate | Amount
1 | Site Clearance(L= d+2*2.0m,B=d+1m) |  |  | 7 | 5 |  | 35 | m² | 137.54 | 4813.9
2 | Earthwork in excavation for foundation in hard soil
| Valve Chamber |  |  | 1.7 | 1.5 | 1.3 | 3.315
| Storage tank | π | 2.3 | 2.3 | - | 1.55 | 25.7595
(Q = p x R² x h, R = d/2+0.05+0.75
| Total | [5 empty] | 29.0745 | m³ | 1362.18 | 39604.6874
3 | Earthwork in back filling with
| in storage tank : total trench (p*R2*h') | π | 2.3 | 2.3 | - | 1.05 | 17.45 | m³
| Deduct tank portion (p*r2*h'): r=d/2+.05 | π | 1.55 | 1.55 | - | 1.05 | -7.9251 | m³
| Net backfilling work | [5 empty] | 9.5249 | m³ | 686.54 | 6539.236
4 | Stone soling work
| Valve Chamber |  |  | 1.7 | 1.5 | 0.15 | 0.3825
| Storage tank | π | 1.8 | 1.8 | - | 0.2 | 2.0358
(Q = p x r² x h, r = d/2+0.05+0.25
| deduction for overlapping with VC portion |  |  | 1.7 | 0.4 | 0.2 | -0.136
| Total | [5 empty] | 2.2823 | m³ | 5141.87 | 11735.0433
5 | Stone masonry in 1:6 c-s mortar
| Valve Chamber |  |  | 5 | 0.35 | 1.15 | 2.0125 | m³ | 14084.92 | 28345.9015
6 | Plain cement concrete (1:2:4)
| Cover slab of valve chamber |  |  | 1.7 | 1.5 | 0.1 | 0.255
| Deduction for manhole opening | π | 0.3 | 0.3 | - | 0.05 | -0.014137
(Q = p x r² x h, r = 0.30)
| Manhole Cover of tank | π | 0.3 | 0.3 | - | 0.05 | 0.014137
| Pipe embeddment block | 2 |  | 1 | 0.35 | 0.2 | 0.14
| Total | [5 empty] | 0.395 | m³ | 15694.9 | 6199.4855
7 | Plain Cement Concrete (1:1.5:3)
| for tank base(Q = p x r² x h, r = d/2+0.05+0.10 | π | 1.65 | 1.65 | - | 0.125 | 1.0691 | m³ | 16948.41 | 18119.9392
8 | Steel reinforcement
for VC slab cover 8 mmf bars @ 15 cm c/c both ways
| Longer span | 11 | 1.7 |  | 0.395 |  | 7.39
| Shorter span | 12 | 1.5 |  | 0.395 |  | 7.11
| Deduction for manhole opening | 8 | 0.6 |  | 0.395 |  | -1.9
| Total | [5 empty] | 12.6 | kg | 123.56 | 1556.856
9 | Shuttering works for RCC
| - Cover slab bottom |  |  | 1 | 0.8 |  | 0.8
| Side |  |  | 6.4 | - | 0.1 | 0.64
| Deduction for manhole opening | π | 0.3 | 0.3 |  |  | -0.28274
| Total | [5 empty] | 1.1573 | m² | 1278.27 | 1479.2865
10 | HDPE formwork for ferrocement
| - Wall portion (Q = 2 x p x r x h, r = d/2+.025) | 2π | 1.525 |  | - | 1.65 | 15.8101
| - Roof portion | 2π | 2.5756 |  |  | 0.5 | 8.0916
Q = 2 x p x R x h, R = ((d+.05)² +4h²)/8h,h=dome height
| - Deduction for manhole opening Q=pxr², r=0.30 | π | 0.3 | 0.3 |  |  | -0.28274
| Total form work | [5 empty] | 23.6189 | m² | 459.51 | 10853.1144
[7 empty] | RT size: |  | 10 | m³
S.N. | Description | No. | Radius | Length | Breadth | Height | Quantity | Unit | Rate | Amount
11 | Bar binding work including chicken wire mesh,
| MS bar, GI wire, etc. |  | as per HDPE form work |  |  |  | 23.6189 | m² | 1222.5 | 28874.0885
12 | 12.5 mm thick 1:2 cement-sand plaster
4 layers for ferrocement
| - Wall portion (Q = 4x2 p x r x h, r = d/2+.025) | 4×2π | 1.525 |  |  | 1.65 | 63.2403
| - Roof portion | 4×2π | 2.5756 |  |  | 0.5 | 32.3663
Q = 2 x p x R x h, R = ((d+.05)² +4h²)/8h,h=dome height
| - Deduction for manhole opening | 4×2π | 0.3 | 0.3 |  |  | -1.131
(Q = 4 x p x r², r = 0.60/2 = 0.30)
| Total plaster | [5 empty] | 94.4755 | m² | 527.79 | 49863.2479
13 | 12.5 mm thick 1:3 cement-sand plaster
sand mortar for
| - Floor portion of storage tank | π | 1.5 | 1.5 |  |  | 7.0686 | m² | 485.7 | 3433.211
(Q = p x r², r = d/2)
14 | 12.5 mm thick 1:4 cement-sand plaster
| - Floor portion of valve chamber |  |  | 1 | 0.8 |  | 0.8
| - inner wall of valve chamber |  |  | 3.6 |  | 1.15 | 4.14
| Total plaster | [5 empty] | 4.94 | m² | 478.27 | 2362.6538
15 | 3 mm thick 1:1 cement sand punning
| - Floor portion of storage tank(Q = p x r², r = d/2) | π | 1.5 | 1.5 |  |  | 7.0686
| - Wall portion of storage tank (Q = 2 x p x r x h) | 2π | 1.5 |  |  | 1.65 | 15.5509
| Total punning | [5 empty] | 22.6195 | m² | 332.33 | 7517.1275
16 | Bitumen paint on the buried surface of storage tank
| (Q = 2 x p x r x h, r = d/2+0.05) | 2π | 1.55 |  |  | 1.25 | 12.1737 | m² | 97.89 | 1191.6807
17 | Snowcem paint on exposed surface of storage tank
| - Wall portion | 2π | 1.55 |  |  | 0.4 | 3.8956
(Q = 2 x p x r x h, r = d/2+0.05)
| - Roof portion | 2π | 2.6525 |  |  | 0.5 | 8.3331
(Q = 2xpxRxh, R = (D²+4h²)/8h, D = d+0.10, h= dome height)
| Total | [5 empty] | 12.2286 | m² | 200.01 | 2445.8522
18 | 600 mmf circular metal manhole cover for ferrocement | [5 empty] | 2 | set | 1701.54 | 3403.08
19 | Installation of Pipes & fittings | [5 empty] | 1 | job | 700 | 700
20 | Barbed wire fencing (Type-A) | 1 | 24 |  |  |  | 24 | m | 2445.48 | 58691.52
21 | Entrancce gate in barbed wire fencing (Type-A) | 1 |  |  |  |  | 1 | No | 18402.57 | 18402.57
| Total Amount without VAT | [8 empty] | 306132.4813
| Add Value Added Tax | [7 empty] | 13 | 39797.2226
| Total cost of reservoir tank with fencing and gate | [7 empty] | Rs. | 345929.7039
Ferrocement Storage Tank
20
| Diameter, d = | 4 | m |  |  | Tank wall height, h = | 1.8 | m
| Dome height, = | 0.7 | m |  | For Scheme # no: | 1 |  |  |  | 465422.4998
S.N. | Description | No. | Radius | Length/Radius | Breadth | Height | Qty. | Unit | Rate | Amount
1 | Site Clearance(L= d+2*2.0m,B=d+1m) |  |  | 8 | 6 |  | 48 | m² | 137.54 | 6601.92
2 | Earthwork in excavation for foundation in hard soil
| Valve Chamber |  |  | 1.7 | 1.5 | 1.3 | 3.315
| Storage tank | π | 2.8 | 2.8 | - | 1.7 | 41.8711
(Q = p x R² x h, R = d/2+0.05+0.75
| Total | [5 empty] | 45.1861 | m³ | 1362.18 | 61551.6656
3 | Earthwork in back filling with
| in storage tank : total trench (p*R2*h') | π | 2.8 | 2.8 | - | 1.2 | 29.5561 | m³
| Deduct tank portion (p*r2*h'): r=d/2+.05 | π | 2.05 | 2.05 | - | 1.2 | -15.8431 | m³
| Net backfilling work | [5 empty] | 13.7131 | m³ | 686.54 | 9414.5587
4 | Stone soling work
| Valve Chamber |  |  | 1.7 | 1.5 | 0.15 | 0.3825
| Storage tank | π | 2.3 | 2.3 | - | 0.2 | 3.3238
(Q = p x r² x h, r = d/2+0.05+0.25
| deduction for overlapping with VC portion |  |  | 1.7 | 0.4 | 0.2 | -0.136
| Total | [5 empty] | 3.5703 | m³ | 5141.87 | 18358.0443
5 | Stone masonry in 1:6 c-s mortar
| Valve Chamber |  |  | 5 | 0.35 | 1.15 | 2.0125 | m³ | 14084.92 | 28345.9015
6 | Plain cement concrete (1:2:4)
| Cover slab of valve chamber |  |  | 1.7 | 1.5 | 0.1 | 0.255
| Deduction for manhole opening | π | 0.3 | 0.3 | - | 0.05 | -0.014137
(Q = p x r² x h, r = 0.30)
| Manhole Cover of tank | π | 0.3 | 0.3 | - | 0.05 | 0.014137
| Pipe embeddment block | 2 |  | 1 | 0.35 | 0.2 | 0.14
| Total | [5 empty] | 0.395 | m³ | 15694.9 | 6199.4855
7 | Plain Cement Concrete (1:1.5:3)
| for tank base(Q = p x r² x h, r = d/2+0.05+0.10 | π | 2.15 | 2.15 | - | 0.125 | 1.8153 | m³ | 16948.41 | 30765.6268
8 | Steel reinforcement
for VC slab cover 8 mmf bars @ 15 cm c/c both ways
| Longer span | 11 | 1.7 |  | 0.395 |  | 7.39
| Shorter span | 12 | 1.5 |  | 0.395 |  | 7.11
| Deduction for manhole opening | 8 | 0.6 |  | 0.395 |  | -1.9
| Total | [5 empty] | 12.6 | kg | 123.56 | 1556.856
9 | Shuttering works for RCC
| - Cover slab bottom |  |  | 1 | 0.8 |  | 0.8
| Side |  |  | 6.4 | - | 0.1 | 0.64
| Deduction for manhole opening | π | 0.3 | 0.3 |  |  | -0.28274
| Total | [5 empty] | 1.1573 | m² | 1278.27 | 1479.2865
10 | HDPE formwork for ferrocement
| - Wall portion (Q = 2 x p x r x h, r = d/2+.025) | 2π | 2.025 |  | - | 1.8 | 22.9022
| - Roof portion | 2π | 3.279 |  |  | 0.7 | 14.4219
Q = 2 x p x R x h, R = ((d+.05)² +4h²)/8h,h=dome height
| - Deduction for manhole opening Q=pxr², r=0.30 | π | 0.3 | 0.3 |  |  | -0.28274
| Total form work | [5 empty] | 37.0413 | m² | 459.51 | 17020.8665
[7 empty] | RT size: |  | 20 | m³
S.N. | Description | No. | Radius | Length | Breadth | Height | Quantity | Unit | Rate | Amount
11 | Bar binding work including chicken wire mesh,
| MS bar, GI wire, etc. |  | as per HDPE form work |  |  |  | 37.0413 | m² | 1222.5 | 45283.0392
12 | 12.5 mm thick 1:2 cement-sand plaster
4 layers for ferrocement
| - Wall portion (Q = 4x2 p x r x h, r = d/2+.025) | 4×2π | 2.025 |  |  | 1.8 | 91.6088
| - Roof portion | 4×2π | 3.279 |  |  | 0.7 | 57.6875
Q = 2 x p x R x h, R = ((d+.05)² +4h²)/8h,h=dome height
| - Deduction for manhole opening | 4×2π | 0.3 | 0.3 |  |  | -1.131
(Q = 4 x p x r², r = 0.60/2 = 0.30)
| Total plaster | [5 empty] | 148.1654 | m² | 527.79 | 78200.1972
13 | 12.5 mm thick 1:3 cement-sand plaster
sand mortar for
| - Floor portion of storage tank | π | 2 | 2 |  |  | 12.5664 | m² | 485.7 | 6103.4862
(Q = p x r², r = d/2)
14 | 12.5 mm thick 1:4 cement-sand plaster
| - Floor portion of valve chamber |  |  | 1 | 0.8 |  | 0.8
| - inner wall of valve chamber |  |  | 3.6 |  | 1.15 | 4.14
| Total plaster | [5 empty] | 4.94 | m² | 478.27 | 2362.6538
15 | 3 mm thick 1:1 cement sand punning
| - Floor portion of storage tank(Q = p x r², r = d/2) | π | 2 | 2 |  |  | 12.5664
| - Wall portion of storage tank (Q = 2 x p x r x h) | 2π | 2 |  |  | 1.8 | 22.6195
| Total punning | [5 empty] | 35.1858 | m² | 332.33 | 11693.3094
16 | Bitumen paint on the buried surface of storage tank
| (Q = 2 x p x r x h, r = d/2+0.05) | 2π | 2.05 |  |  | 1.4 | 18.0327 | m² | 97.89 | 1765.2251
17 | Snowcem paint on exposed surface of storage tank
| - Wall portion | 2π | 2.05 |  |  | 0.4 | 5.1522
(Q = 2 x p x r x h, r = d/2+0.05)
| - Roof portion | 2π | 3.3518 |  |  | 0.7 | 14.7419
(Q = 2xpxRxh, R = (D²+4h²)/8h, D = d+0.10, h= dome height)
| Total | [5 empty] | 19.8941 | m² | 200.01 | 3979.026
18 | 600 mmf circular metal manhole cover for ferrocement | [5 empty] | 2 | set | 1701.54 | 3403.08
19 | Installation of Pipes & fittings | [5 empty] | 1 | job | 700 | 700
20 | Barbed wire fencing (Type-A) | 1 | 24 |  |  |  | 24 | m | 2445.48 | 58691.52
21 | Entrancce gate in barbed wire fencing (Type-A) | 1 |  |  |  |  | 1 | No | 18402.57 | 18402.57
| Total Amount without VAT | [8 empty] | 411878.3184
| Add Value Added Tax | [7 empty] | 13 | 53544.1814
| Total cost of reservoir tank with fencing and gate | [7 empty] | Rs. | 465422.4998
Ferrocement Storage Tank
16
| Diameter, d = | 3.5 | m |  |  | Tank wall height, h = | 1.9 | m
| Dome height, = | 0.6 | m |  | For Scheme # no: | 1 |  |  |  | 419395.9378
S.N. | Description | No. | Radius | Length/Radius | Breadth | Height | Qty. | Unit | Rate | Amount
1 | Site Clearance(L= d+2*2.0m,B=d+1m) |  |  | 8 | 6 |  | 48 | m² | 137.54 | 6601.92
2 | Earthwork in excavation for foundation in hard soil
| Valve Chamber |  |  | 1.7 | 1.5 | 1.3 | 3.315
| Storage tank | π | 2.55 | 2.55 | - | 1.8 | 36.7708
(Q = p x R² x h, R = d/2+0.05+0.75
| Total | [5 empty] | 40.0858 | m³ | 1362.18 | 54604.0358
3 | Earthwork in back filling with
| in storage tank : total trench (p*R2*h') | π | 2.55 | 2.55 | - | 1.3 | 26.5567 | m³
| Deduct tank portion (p*r2*h'): r=d/2+.05 | π | 1.8 | 1.8 | - | 1.3 | -13.2324 | m³
| Net backfilling work | [5 empty] | 13.3243 | m³ | 686.54 | 9147.6511
4 | Stone soling work
| Valve Chamber |  |  | 1.7 | 1.5 | 0.15 | 0.3825
| Storage tank | π | 2.05 | 2.05 | - | 0.2 | 2.6405
(Q = p x r² x h, r = d/2+0.05+0.25
| deduction for overlapping with VC portion |  |  | 1.7 | 0.4 | 0.2 | -0.136
| Total | [5 empty] | 2.887 | m³ | 5141.87 | 14844.623
5 | Stone masonry in 1:6 c-s mortar
| Valve Chamber |  |  | 5 | 0.35 | 1.15 | 2.0125 | m³ | 14084.92 | 28345.9015
6 | Plain cement concrete (1:2:4)
| Cover slab of valve chamber |  |  | 1.7 | 1.5 | 0.1 | 0.255
| Deduction for manhole opening | π | 0.3 | 0.3 | - | 0.05 | -0.014137
(Q = p x r² x h, r = 0.30)
| Manhole Cover of tank | π | 0.3 | 0.3 | - | 0.05 | 0.014137
| Pipe embeddment block | 2 |  | 1 | 0.35 | 0.2 | 0.14
| Total | [5 empty] | 0.395 | m³ | 15694.9 | 6199.4855
7 | Plain Cement Concrete (1:1.5:3)
| for tank base(Q = p x r² x h, r = d/2+0.05+0.10 | π | 1.9 | 1.9 | - | 0.125 | 1.4176 | m³ | 16948.41 | 24026.8064
8 | Steel reinforcement
for VC slab cover 8 mmf bars @ 15 cm c/c both ways
| Longer span | 11 | 1.7 |  | 0.395 |  | 7.39
| Shorter span | 12 | 1.5 |  | 0.395 |  | 7.11
| Deduction for manhole opening | 8 | 0.6 |  | 0.395 |  | -1.9
| Total | [5 empty] | 12.6 | kg | 123.56 | 1556.856
9 | Shuttering works for RCC
| - Cover slab bottom |  |  | 1 | 0.8 |  | 0.8
| Side |  |  | 6.4 | - | 0.1 | 0.64
| Deduction for manhole opening | π | 0.3 | 0.3 |  |  | -0.28274
| Total | [5 empty] | 1.1573 | m² | 1278.27 | 1479.2865
10 | HDPE formwork for ferrocement
| - Wall portion (Q = 2 x p x r x h, r = d/2+.025) | 2π | 1.775 |  | - | 1.9 | 21.19
| - Roof portion | 2π | 2.9255 |  |  | 0.6 | 11.029
Q = 2 x p x R x h, R = ((d+.05)² +4h²)/8h,h=dome height
| - Deduction for manhole opening Q=pxr², r=0.30 | π | 0.3 | 0.3 |  |  | -0.28274
| Total form work | [5 empty] | 31.9363 | m² | 459.51 | 14675.0275
[7 empty] | RT size: |  | 16 | m³
S.N. | Description | No. | Radius | Length | Breadth | Height | Quantity | Unit | Rate | Amount
11 | Bar binding work including chicken wire mesh,
| MS bar, GI wire, etc. |  | as per HDPE form work |  |  |  | 31.9363 | m² | 1222.5 | 39042.0691
12 | 12.5 mm thick 1:2 cement-sand plaster
4 layers for ferrocement
| - Wall portion (Q = 4x2 p x r x h, r = d/2+.025) | 4×2π | 1.775 |  |  | 1.9 | 84.7602
| - Roof portion | 4×2π | 2.9255 |  |  | 0.6 | 44.1158
Q = 2 x p x R x h, R = ((d+.05)² +4h²)/8h,h=dome height
| - Deduction for manhole opening | 4×2π | 0.3 | 0.3 |  |  | -1.131
(Q = 4 x p x r², r = 0.60/2 = 0.30)
| Total plaster | [5 empty] | 127.745 | m² | 527.79 | 67422.5395
13 | 12.5 mm thick 1:3 cement-sand plaster
sand mortar for
| - Floor portion of storage tank | π | 1.75 | 1.75 |  |  | 9.6211 | m² | 485.7 | 4672.9816
(Q = p x r², r = d/2)
14 | 12.5 mm thick 1:4 cement-sand plaster
| - Floor portion of valve chamber |  |  | 1 | 0.8 |  | 0.8
| - inner wall of valve chamber |  |  | 3.6 |  | 1.15 | 4.14
| Total plaster | [5 empty] | 4.94 | m² | 478.27 | 2362.6538
15 | 3 mm thick 1:1 cement sand punning
| - Floor portion of storage tank(Q = p x r², r = d/2) | π | 1.75 | 1.75 |  |  | 9.6211
| - Wall portion of storage tank (Q = 2 x p x r x h) | 2π | 1.75 |  |  | 1.9 | 20.8916
| Total punning | [5 empty] | 30.5127 | m² | 332.33 | 10140.2918
16 | Bitumen paint on the buried surface of storage tank
| (Q = 2 x p x r x h, r = d/2+0.05) | 2π | 1.8 |  |  | 1.5 | 16.9646 | m² | 97.89 | 1660.6647
17 | Snowcem paint on exposed surface of storage tank
| - Wall portion | 2π | 1.8 |  |  | 0.4 | 4.5239
(Q = 2 x p x r x h, r = d/2+0.05)
| - Roof portion | 2π | 3 |  |  | 0.6 | 11.3097
(Q = 2xpxRxh, R = (D²+4h²)/8h, D = d+0.10, h= dome height)
| Total | [5 empty] | 15.8336 | m² | 200.01 | 3166.8837
18 | 600 mmf circular metal manhole cover for ferrocement | [5 empty] | 2 | set | 1701.54 | 3403.08
19 | Installation of Pipes & fittings | [5 empty] | 1 | job | 700 | 700
20 | Barbed wire fencing (Type-A) | 1 | 24 |  |  |  | 24 | m | 2445.48 | 58691.52
21 | Entrancce gate in barbed wire fencing (Type-A) | 1 |  |  |  |  | 1 | No | 18402.57 | 18402.57
| Total Amount without VAT | [8 empty] | 371146.8476
| Add Value Added Tax | [7 empty] | 13 | 48249.0902
| Total cost of reservoir tank with fencing and gate | [7 empty] | Rs. | 419395.9378

## vc-bpt (hidden)
Air Valve Chamber
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rate | Amount
1 | Site clearance |  | 1.5 | 1.5 |  | 2.25 |  | 137.54 | 309.465
2 | Earthwork in excavation for foundation in BMS
|  | 1 | 1 | 1 | 1.1 | 1.1 | m³ | 1362.18 | 1498.398
3 | Dry stone filling | 1 | 1 | 1 | 0.4 | 0.4 | m³ | 5141.87 | 2056.748
4 | Stone masonry in 1:6 c-s mortar | 1 | 2.6 | 0.35 | 0.6 | 0.546 | m³ | 14084.92 | 7690.3663
5 | Plain Cement Concrete (1:2:4)
| Slab cover | 1 | 1 | 1 | 0.08 | 0.08
| Deduction for manhole opening | π | 0.23 | 0.23 | 0.08 | -0.013295
| Manhole cover | π | 0.23 | 0.23 | 0.05 | 0.0083095
| Total |  |  |  |  | 0.075014 | m³ | 15694.9 | 1177.3418
6 | Centering & Shuttering Works | 1 | 4 | - | 0.08 | 0.32 | m² | 1278.27 | 409.0464
7 | Selected material filling (stone Packing) | 1 | 1 | 1 | 0.25 | 0.25 | m³ | 5141.87 | 1285.4675
8 | Standard manhole cover 45×45 cm with metal frame |  |  |  |  | 1 | no. | 1869.21 | 1869.21
9 | Installation of pipes & fittings |  |  |  |  | 1 | job | 600 | 600
| Subtotal | [7 empty] | 16896.043
| Add Value Added Tax | [6 empty] | 13 | 2196.4856
| Total Amount with VAT | [6 empty] | Rs. | 19092.5286
Valve Chamber
Sankhu Drinking Water Supply Project
| Inner dimension | 1 | m x | 0.6 | m
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rate | Amount
1 | Site Clearance |  | 2 | 2 |  | 4 |  | 137.54 | 550.16
2 | Earthwork in excavation for foundation
|  | 1 | 1.7 | 1.3 | 1.3 | 2.873 | m³ | 1362.18 | 3913.5431
3 | Boulder soling | 1 | 1.7 | 1.3 | 0.15 | 0.3315 | m³ | 5141.87 | 1704.5299
4 | Stone masonry in 1:6 c-s mortar |  | 4.6 | 0.35 | 1 | 1.61 | m³ | 14084.92 | 22676.7212
5 | Plain Cement Concrete (1:2:4)
| Cover slab | 1 | 1.7 | 1.3 | 0.1 | 0.22
| Deduction for manhole |  | 0.6 | 0.6 | 0.1 | -0.1131
| Manhole cover |  | 0.6 | 0.6 | 0.05 | 0.056549
| Total |  |  |  |  | 0.16345 | m³ | 15694.9 | 2565.3523
6 | Steel reinforcement
8 mm ø at 150 mm spacing bothways
| Longer span | 12 | 1.3 | 0.395 |  | 6.16
| Shorter span | 10 | 1.7 | 0.395 |  | 6.72
| Deduction for manhole opening | 12 | 0.45 | 0.395 |  | -2.13
| Total |  |  |  |  | 10.75 | kg | 123.56 | 1328.27
7 | Centering & Shuttering work for RCC
| Cover slab bottom | 1 | 1 | 0.6 | - | 0.6
| Sides | 1 | 6 | - | 0.1 | 0.6
| Deduction for manhole opening | 1 | 0.75 | 0.75 | - | -0.5625
[6 empty] | 0.6375 | m² | 1278.27 | 814.8971
8 | Standard manhole cover 60*60 cm with metal frame |  |  |  |  | 1 | no. | 2452.95 | 2452.95
9 | Installation of pipes & fittings |  |  |  |  | 1 | job | 800 | 800
| Subtotal | [7 empty] | 36806.4237
| Add Value Added Tax | [6 empty] | 13 | 4784.8351
| Total Amount with VAT | [6 empty] | Rs. | 41591.2588
BREAK PRESSURE CHAMBER
( Without valve chamber )
| Inner size of BPT portion: | 0.8 | x | 0.8 | Total height= |  | 0.8
S.N. | Description | No. | Length | Breadth | Height | Quantity | Unit | Rate | Amount
1 | Site clearance |  | 2.5 | 2.5 |  | 6.25 | m² | 137.54 | 859.63
2 | Earthwork in excavation
|  | 1 | 1.7 | 1.7 | 0.7 | 2.023 | m³ | 1362.18 | 2755.69
3 | Boulder soling | 1 | 1.7 | 1.7 | 0.15 | 0.4335 | m³ | 5141.87 | 2229
4 | Plain Cement Concrete (1:2:4)
| in foundation | 1 | 1.7 | 1.7 | 0.1 | 0.289
| Pipe embeddment block | 4 | 0.45 | 0.2 | 0.2 | 0.072
| Cover slab | 1 | 1.7 | 1.7 | 0.1 | 0.289
Deduct:
| -Manhole cover | 1 | 0.6 | 0.6 | 0.05 | -0.018
| Total |  |  |  |  | 0.632 | m³ | 15694.9 | 9919.18
5 | Stone masonry work in 1:4 c-s mortar
|  | 1 | 5 | 0.45 | 0.8 | 1.8
| Deduct for pipe embeddment block | 4 | 0.45 | 0.2 | 0.2 | -0.072
| Total |  |  |  |  | 1.728 | m³ | 14865.17 | 25687.01
6 | Centering & shuttering works
| Bottom of cover slab | 1 | 0.8 | 0.8 |  | 0.64
| -Outer edge of cover slab | 1 | 6.8 |  | 0.1 | 0.68
| Total |  |  |  |  | 1.32 | m² | 1278.27 | 1687.32
7 | Steel reinforcement (for cover slab)
| 8 mm ø @ 150 mm c/c bothways | 12 | 1.7 | 0.395 |  | 8.058
|  | 12 | 1.7 | 0.395 |  | 8.058
| Deduct for man hole | 8 | 0.6 | 0.395 |  | -1.896
| Total |  |  |  |  | 14.22 | kg | 123.56 | 1757.02
8 | 12.5 mm thick 1:4 c-s plaster
| floor | 1 | 0.8 | 0.8 |  | 0.64
| Inner sides of Walls | 2 | 0.8 | - | 0.8 | 1.28
|  | 2 | 0.8 | - | 0.8 | 1.28
| Outer Portion of all walls above GL | 1 | 6.8 | - | 0.35 | 2.38
| Total |  |  |  |  | 5.58 | m² | 478.27 | 2668.75
9 | 3 mm 1:1 c-s punning
| -Inner side of BPT |  |  |  |  | 3.2 | m² | 332.33 | 1063.46
10 | Standard manhole cover 60x60 cm ø with metal frame |  |  |  |  | 1 | set | 2452.95 | 2452.95
11 | Installation of pipes and fittings |  |  |  |  | 1 | job | 800 | 800
| Subtotal | [7 empty] | 51880.01
| Add Value Added Tax | [6 empty] | 13 | 6744.4013
| Total Amount with VAT | [6 empty] | Rs. | 58624.4113

## tools (hidden)
Procurement of Tools & Plants
[5 empty] | Total | Unit Price | Amount
Sn | Type of Tools | Unit | Qty | Wt/Unit | Wt | 2072/73
|  |  |  | kg | kg | (Rs) | (Rs)
1 | Shovel | Pc | 10 | 2.4 | 24 | 535 | 5350
2 | Pick Axe | Pc | 10 | 5 | 50 | 523 | 5230
3 | Hoe | Pc | 10 | 2 | 20 | 330 | 3300
2 | Crowbar 1" x 5" | Pc | 6 | 3.5 | 21 | 1660 | 9960
3 | Sledge Hammer 10 lbs | Pc | 4 | 4.55 | 18.2 | 1160 | 4640
4 | Stone Chisel 1" x 6" | Pc | 4 | 1 | 4 | 357 | 1428
3 | Stone Chisel 1" x 12" | Pc | 4 | 2 | 8 | 620 | 2480
4 | Tools Box with locking set | Pc | 4 | 10 | 40 | 1593 | 6372
5 | Heating Plate (100 mm dia.) | Pc | 4 | 2.5 | 10 | 655.2 | 2620.8
4 | Heating Plate (150 mm dia.) | Pc | 4 | 3.5 | 14 | 1542 | 6168
5 | Teflon Cover (18cm x 18cm - bag size) | Rm | 1 | 0.01 | 0.01 | 450 | 450
6 | Thermocrome Crayon | Pc | 1 |  | 0 | 4338 | 4338
5 | Blow Torch | Pc | 4 | 1 | 4 | 960 | 3840
6 | Thread seal tape | Pc | 30 |  | 0 | 15 | 450
7 | Pipe Wrench 36" | Pc | 4 | 3 | 12 | 2956.8 | 11827.2
6 | Pipe Wrench 24" | Pc | 4 | 2.5 | 10 | 1575 | 6300
7 | Pipe Wrench 14" | Pc | 4 | 1.5 | 6 | 739.2 | 2956.8
8 | Pipe Wrench 18" | Pc | 4 | 2.4 | 9.6 | 1050 | 4200
7 | Pipe Wrench 12" | Pc | 4 | 2.4 | 9.6 | 513.6 | 2054.4
8 | Hacksaw Frame | Pc | 4 | 0.6 | 2.4 | 175 | 700
9 | Hacksaw Blade | dz. | 4 | 0.5 | 2 | 72 | 288
8 | Adjustable Spanner 18" | Pc | 4 | 0.4 | 1.6 | 365 | 1460
9 | Iron Pan (medium size) | Pc | 4 | 1 | 4 | 300 | 1200
10 | Building Trowel | Pc | 4 | 0.25 | 1 | 90 | 360
9 | Pointing Trowel | Pc | 4 | 0.1 | 0.4 | 75 | 300
10 | Iron Brush | Pc | 4 | 0.5 | 2 | 84 | 336
11 | Die Set ½"-1" with teeth | Set | 2 | 0.8 | 1.6 | 4113.6 | 8227.2
10 | Die Set 1½"-2½" with teeth | Set | 2 | 1 | 2 | 8740.8 | 17481.6
11 | Spare Die Teeth (½"-2½") | Set | 2 | 0.5 | 1 | 2887.2 | 5774.4
12 | Spare Die Teeth (3"-4") | Set | 2 | 0.5 | 1 | 1645.2 | 3290.4
11 | Die Teeth Oil with cane | Lt. | 2 | 1.5 | 3 | 164.4 | 328.8
12 | Measuring Tape(fibre glass) 30 m. | Pc | 2 | 0.75 | 1.5 | 800 | 1600
|  |  |  | Sub-Total | 283.91 |  | 125311.6
| Add Value Added Tax |  |  |  |  | 13 | 16290.508
| Total |  |  |  |  | Rs. | 141602.108

## FittingsSummary (hidden)
Scheme No: |  | 1
Scheme Name : |  | Scheme 1
Summary of structurewise fittings
SN | Description | ItemCode | Units | BPT-01 | IC-01 | CoC-01 | CoC-02 | CoC-03 | DiC-01 | DiC-02 | #REF! | #REF! | #REF! | #REF! | SINT-01 | SINT-02 | SINT-03 | S-VaC-J1 | W-VaC-J5 | A-VaC-J40 | VaC-J50 | VaC-J51 | VaC-J57 | TotalQty | UnitWt(kg) | TotalWt(Kg) | Rate(Rs) | TotalAmount(Rs)
|  |  | Nos | 6 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 6 | 6 | 5 | 0 | 0 | 0
1 | Brass Union (15x20 mmØ) | BU-15 | no | [11 empty] | 2 | [8 empty] | 2 | 0.13 | 0.26 | 455 | 910
2 | Brass Union (20x25 mmØ) | BU-20 | no | [14 empty] | 4 | 4 |  |  |  |  | 48 | 0.18 | 8.64 | 484 | 23232
3 | Brass Union (25x32 mmØ) | BU-25 | no | 5 |  | 2 | [12 empty] | 4 | 4 |  |  |  | 78 | 0.25 | 19.5 | 717 | 55926
4 | Brass Union (32x40 mmØ) | BU-32 | no | 3 | [13 empty] | 6 |  | 4 |  |  |  | 74 | 0.37 | 27.38 | 979 | 72446
5 | Brass Union (40x50 mmØ) | BU-40 | no |  |  | 1 | [11 empty] | 2 | [5 empty] | 14 | 0.5 | 7 | 1469 | 20566
6 | GI Blind flange set (100 mmØ) | GBF-100 | set | [20 empty] | 0 | 6 | 0 | 2121 | 0
7 | GI Blind flange set (65 mmØ) | GBF-65 | set | [20 empty] | 0 | 3.75 | 0 | 1532 | 0
8 | GI Elbow (100 mmØ) | GEL-100 | no | [20 empty] | 0 | 1.97 | 0 | 1320 | 0
9 | GI Elbow (15 mmØ) | GEL-15 | no | [10 empty] | 4 | 1 | [8 empty] | 9 | 0.1 | 0.9 | 34 | 306
10 | GI Elbow (20 mmØ) | GEL-20 | no | [20 empty] | 0 | 0.2 | 0 | 86 | 0
11 | GI Elbow (25 mmØ) | GEL-25 | no | 6 |  | 6 | [17 empty] | 48 | 0.2 | 9.6 | 86 | 4128
12 | GI Elbow (32 mmØ) | GEL-32 | no | 3 | [19 empty] | 18 | 0.3 | 5.4 | 133 | 2394
13 | GI Elbow (40 mmØ) | GEL-40 | no | 6 | [9 empty] | 3 | [9 empty] | 42 | 0.4 | 16.8 | 184 | 7728
14 | GI Elbow (50 mmØ) | GEL-50 | no | 3 | [9 empty] | 8 | [9 empty] | 34 | 0.68 | 23.12 | 284 | 9656
15 | GI Elbow (63 mmØ) | GEL-65 | no |  |  | 3 |  |  | 3 | [14 empty] | 9 | 1.07 | 9.63 | 539 | 4851
16 | GI Elbow (75 mmØ) | GEL-80 | no |  |  | 2 |  |  | 2 | [14 empty] | 6 | 1.46 | 8.76 | 730 | 4380
17 | GI Equal Tee (100 mmØ) | GET-100 | no | [20 empty] | 0 | 2.25 | 0 | 1528 | 0
18 | GI Equal Tee (15 mmØ) | GET-15 | no | 6 |  | 2 |  |  | 1 | [14 empty] | 41 | 0.13 | 5.33 | 54 | 2214
19 | GI Equal Tee (20 mmØ) | GET-20 | no | [20 empty] | 0 | 1.75 | 0 | 78 | 0
20 | GI Equal Tee (25 mmØ) | GET-25 | no |  |  | 2 | [8 empty] | 2 | [8 empty] | 6 | 1.75 | 10.5 | 226 | 1356
21 | GI Equal Tee (32 mmØ) | GET-32 | no | [20 empty] | 0 | 1.75 | 0 | 275 | 0
22 | GI Equal Tee (40 mmØ) | GET-40 | no | [20 empty] | 0 | 1.75 | 0 | 431 | 0
23 | GI Equal Tee (80 mmØ) | GET-80 | no | [20 empty] | 0 | 1.75 | 0 | 678 | 0
24 | GI Equal Tee(40 mmØ) | GET-40 | no | [20 empty] | 0 | 0.5 | 0 | 220 | 0
25 | GI Nipple (100 mmØ) | GNI-100 | no | [20 empty] | 0 | 2.45 | 0 | 697 | 0
26 | GI Nipple (15 mmØ) | GNI-15 | no | [10 empty] | 2 | 2 |  |  |  | 4 |  |  |  |  | 30 | 0.13 | 3.9 | 38 | 1140
27 | GI Nipple (20 mmØ) | GNI-20 | no | [20 empty] | 0 | 0.2 | 0 | 62 | 0
28 | GI Nipple (25 mmØ) | GNI-25 | no | 3 |  | 4 | [12 empty] | 4 | 4 |  |  |  | 70 | 0.25 | 17.5 | 82 | 5740
29 | GI Nipple (32 mmØ) | GNI-32 | no | 2 | [19 empty] | 12 | 0.28 | 3.36 | 117 | 1404
30 | GI Nipple (40 mmØ) | GNI-40 | no | 1 | [14 empty] | 2 | 4 |  |  |  | 38 | 0.3 | 11.4 | 182 | 6916
31 | GI Nipple (50 mmØ) | GNI-50 | no | 1 | [9 empty] | 8 |  |  |  |  | 2 |  |  |  |  | 34 | 0.4 | 13.6 | 241 | 8194
32 | GI Nipple (65 mmØ) | GNI-63 | no | [16 empty] | 2 |  |  |  | 10 | 0.7 | 7 | 315 | 3150
33 | GI Nipple (80 mmØ) | GNI-80 | no | [5 empty] | 1 | [14 empty] | 1 | 1.75 | 1.75 | 525 | 525
34 | GI Pipe (100mm)-MC | GPM-100 | m | [20 empty] | 0 | 12.99 | 0 | 1265 | 0
35 | GI Pipe (15mm)-MC | GPM-15 | m | 8.7 |  | 2.9 |  |  | 1.45 |  |  |  |  | 5.3 | [9 empty] | 70.05 | 1.28 | 89.664 | 134 | 9386.7
36 | GI Pipe (20mm)-MC | GPM-20 | m | [20 empty] | 0 | 1.66 | 0 | 170 | 0
37 | GI Pipe (25mm)-MC | GPM-25 | m | 9.18 |  | 3.85 | [17 empty] | 62.78 | 2.53 | 158.8334 | 259 | 16260.02
38 | GI Pipe (32mm)-MC | GPM-32 | m | 5.59 | [19 empty] | 33.54 | 3.28 | 110.0112 | 337 | 11302.98
39 | GI Pipe (40mm)-MC | GPM-40 | m | 5.18 |  | 2 |  |  | 2 |  |  |  |  | 3.2 | [9 empty] | 43.48 | 3.79 | 164.7892 | 387 | 16826.76
40 | GI Pipe (50mm)-MC | GPM-50 | m | 6.89 |  | 1.1 | [7 empty] | 16.7 | [9 empty] | 76.94 | 5.32 | 409.3208 | 532 | 40932.08
41 | GI Pipe (63mm)-MC | GPM-65 | m | [5 empty] | 7.34 | [14 empty] | 7.34 | 6.35 | 46.609 | 679 | 4983.86
42 | GI Pipe (75mm)-MC | GPM-80 | m | [5 empty] | 12.65 | [14 empty] | 12.65 | 8.85 | 111.9525 | 845 | 10689.25
43 | GI Plug (40 mmØ) | GIP-40 | no | [20 empty] | 0 | 1 | 0 | 66 | 0
44 | GI Plug (50 mmØ) | GIP-50 | no | [20 empty] | 0 | 1 | 0 | 101 | 0
45 | GI Reducer Socket (100x40 mmØ) | GRS-100x40 | no | [20 empty] | 0 | 0.65 | 0 | 895 | 0
46 | GI Reducer Socket (100x80 mmØ) | GRS-100x80 | no | [20 empty] | 0 | 0.95 | 0 | 895 | 0
47 | GI Reducer Socket (125x100 mmØ) | GRS-125x100 | no | [20 empty] | 0 | 1 | 0 | 895 | 0
48 | GI Reducer Socket (32x25 mmØ) | GRS-32x25 | no | [20 empty] | 0 | 0.65 | 0 | 108 | 0
49 | GI Reducer Socket (40x32 mmØ) | GRS-40x32 | no | [20 empty] | 0 | 0.65 | 0 | 134 | 0
50 | GI Reducer Socket (50x40 mmØ) | GRS-50x40 | no | [20 empty] | 0 | 0.65 | 0 | 224 | 0
51 | GI Reducer Socket (65x50 mmØ) | GRS-65x50 | no | [20 empty] | 0 | 0.65 | 0 | 366 | 0
52 | GI Reducer Socket (80x40 mmØ) | GRS-80x40 | no | [20 empty] | 0 | 0.65 | 0 | 895 | 0
53 | GI Socket 100 mmØ | GS-100 | no | [20 empty] | 0 | 1.5 | 0 | 782 | 0
54 | GI Socket 15 mmØ | GS-15 | no | [11 empty] | 1 | [8 empty] | 1 | 0.08 | 0.08 | 30 | 30
55 | GI Socket 25 mmØ | GS-25 | no | [20 empty] | 0 | 0.15 | 0 | 62 | 0
56 | GI Socket 40 mmØ | GS-40 | no | [20 empty] | 0 | 0.25 | 0 | 118 | 0
57 | GI Socket 50 mmØ | GS-50 | no | [20 empty] | 0 | 0.5 | 0 | 197 | 0
58 | GI Socket 75 mmØ | GS-80 | no | [5 empty] | 1 | [14 empty] | 1 | 1.13 | 1.13 | 483 | 483
59 | GI Unequal Tee (100x15 mmØ) | GUT-100x15 | no | [20 empty] | 0 | 1.5 | 0 | 1500 | 0
60 | GI Unequal Tee (100x25 mmØ) | GUT-100x25 | no | [20 empty] | 0 | 1.6 | 0 | 1500 | 0
61 | GI Unequal Tee (100x40 mmØ) | GUT-100x40 | no | [20 empty] | 0 | 1.7 | 0 | 1500 | 0
62 | GI Unequal Tee (100x50 mmØ) | GUT-100x50 | no | [20 empty] | 0 | 1.75 | 0 | 1500 | 0
63 | GI Unequal Tee (100x80 mmØ) | GUT-100x80 | no | [20 empty] | 0 | 1.95 | 0 | 1500 | 0
64 | GI Unequal Tee (25x15 mmØ) | GUT-25x15 | no | 3 | [15 empty] | 2 |  |  |  | 28 | 0.23 | 6.44 | 140 | 3920
65 | GI Unequal Tee (32x15 mmØ) | GUT-32x15 | no | 2 | [19 empty] | 12 | 0.23 | 2.76 | 209 | 2508
66 | GI Unequal Tee (40x15 mmØ) | GUT-40x15 | no | 1 |  | 1 | [13 empty] | 2 |  |  |  | 18 | 0.4 | 7.2 | 278 | 5004
67 | GI Unequal Tee (50x15 mmØ) | GUT-50x15 | no | 1 | [9 empty] | 2 | [9 empty] | 10 | 0.5 | 5 | 439 | 4390
68 | GI Unequal Tee (80x15 mmØ) | GUT-80x15 | no |  |  | 1 | [17 empty] | 2 | 0.85 | 1.7 | 1216 | 2432
69 | GI Unequal Tee (80x20 mmØ) | GUT-80x20 | no | [16 empty] | 1 |  |  |  | 5 | 0.9 | 4.5 | 1216 | 6080
70 | GI Unequal Tee (80x40 mmØ) | GUT-80x40 | no | [20 empty] | 0 | 1.05 | 0 | 1216 | 0
71 | GI Unequal Tee (80x50 mmØ) | GUT-80x50 | no | [20 empty] | 0 | 1.1 | 0 | 1216 | 0
72 | GI Union (15 mmØ) | GUN-15 | no | [10 empty] | 2 | [9 empty] | 4 | 0.22 | 0.88 | 92 | 368
73 | GI Union (20 mmØ) | GUN-20 | no | [20 empty] | 0 | 0.26 | 0 | 118 | 0
74 | GI Union (25 mmØ) | GUN-25 | no | 3 | [19 empty] | 18 | 0.3 | 5.4 | 170 | 3060
75 | GI Union (32 mmØ) | GUN-32 | no | 2 | [19 empty] | 12 | 0.5 | 6 | 270 | 3240
76 | GI Union (40 mmØ) | GUN-40 | no | 1 | [19 empty] | 6 | 0.65 | 3.9 | 328 | 1968
77 | GI Union (50 mmØ) | GUN-50 | no | 1 | [9 empty] | 2 | [9 empty] | 10 | 1.13 | 11.3 | 501 | 5010
78 | GI Union (80 mmØ) | GUN-80 | no | [5 empty] | 1 | [14 empty] | 1 | 2.38 | 2.38 | 1309 | 1309
79 | GI-GI flange set (100 mmØ) | GFL-100 | set | [20 empty] | 0 | 3.75 | 0 | 2121 | 0
80 | GI-HDP flange set (100x125 mmØ) | GHF-100 | set | [20 empty] | 0 | 3.75 | 0 | 1768 | 0
81 | GI-HDP flange set (40x50 mmØ) | GHF-50 | set | 3 | [9 empty] | 1 |  |  |  |  | 2 | 2 |  |  |  | 42 | 2.4 | 100.8 | 1196 | 50232
82 | GI-HDP flange set (50x63 mmØ) | GHF-63 | set | 2 |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  | 2 |  |  |  |  | 29 | 2.4 | 69.6 | 1800 | 52200
83 | GI-HDP flange set (80x90 mmØ) | GHF-80 | set | [5 empty] | 1 | [14 empty] | 1 | 3.25 | 3.25 | 1795 | 1795
84 | GI-HDP flange set (75x63 mmØ) | GHF-75 | no | [16 empty] | 2 |  |  |  | 10 | 2.7 | 27 | 2050 | 20500
85 | GM Gate Valve (100 mmØ) | GMGAV-100 | no | [20 empty] | 0 | 5.44 | 0 | 28000 | 0
86 | GM Gate Valve (15 mmØ) | GMGAV-15 | no | [20 empty] | 0 | 0.65 | 0 | 832 | 0
87 | GM Gate Valve (20 mmØ) | GMGAV-20 | no | [14 empty] | 2 | 2 |  |  |  |  | 24 | 1.2 | 28.8 | 1143 | 27432
88 | GM Gate Valve (25 mmØ) | GMGAV-25 | no |  |  | 2 | [11 empty] | 3 | 2 |  |  |  |  | 34 | 1.67 | 56.78 | 1744 | 59296
89 | GM Gate Valve (32 mmØ) | GMGAV-32 | no | [14 empty] | 1 | [5 empty] | 6 | 1.8 | 10.8 | 2624 | 15744
90 | GM Gate Valve (40 mmØ) | GMGAV-40 | no | [15 empty] | 1 |  |  |  |  | 6 | 1.9 | 11.4 | 3537 | 21222
91 | GM Gate Valve (50 mmØ) | GMGAV-50 | no | [10 empty] | 4 |  |  |  |  | 1 |  |  |  |  | 14 | 2.7 | 37.8 | 5500 | 77000
92 | GM Gate Valve (65 mmØ) | BGAV-65 | [6 empty] | `1 | [14 empty] | 0 | 3.1 | 0 | 7299 | 0
93 | GM Gate Valve (80 mmØ) | GMGAV-80 | no | [20 empty] | 0 | 4.25 | 0 | 16000 | 0
94 | GM Globe Valve (100 mmØ) | GMGLV-100 | no | [20 empty] | 0 | 1 | 0 | 28293 | 0
95 | GM Globe Valve (15 mmØ) | GMGLV-15 | no | [20 empty] | 0 | 0.88 | 0 | 761 | 0
96 | GM Globe Valve (20 mmØ) | GMGLV-20 | no | [20 empty] | 0 | 0.96 | 0 | 1262 | 0
97 | GM Globe Valve (25 mmØ) | GMGLV-25 | no | 2 | [19 empty] | 12 | 1.38 | 16.56 | 1660 | 19920
98 | GM Globe Valve (32 mmØ) | GMGLV-32 | no | 1 | [19 empty] | 6 | 1.88 | 11.28 | 3214 | 19284
99 | GM Globe Valve (40 mmØ) | GMGLV-40 | no | 2 | [19 empty] | 12 | 2.38 | 28.56 | 4285 | 51420
100 | GM Globe Valve (50 mmØ) | GMGLV-50 | no | 1 | [19 empty] | 6 | 2.88 | 17.28 | 5892 | 35352
101 | GM Globe Valve (80 mmØ) | GMGLV-80 | no | [20 empty] | 0 | 1 | 0 | 16605 | 0
102 | G.I. Bracket 1/2" | GBR-15 |  | 6 |  | 2 |  |  | 1 | [14 empty] | 41 | 0.14 | 5.74 | 31 | 1271
103 | G.I. Bracket 1" | GBR-25 |  | 2 |  | 2 | [17 empty] | 16 | 0.17 | 2.72 | 87 | 1392
104 | G.I. Bracket 1-1/4" | GBR-32 |  | 1 | [19 empty] | 6 | 0.21 | 1.26 | 99 | 594
105 | G.I. Bracket 1-1/2" | GBR-40 |  | 2 | [19 empty] | 12 | 0.35 | 4.2 | 101 | 1212
106 | G.I. Bracket 2" | GBR-50 |  | 1 | [19 empty] | 6 | 0.45 | 2.7 | 300 | 1800
107 | G.I. Bracket 2-1/2" | GBR-63 | 1 | [5 empty] | 1 | [14 empty] | 1 | 0.7 | 0.7 | 481 | 481
108 | G.I. Mouth Piece (2") | GMP-63 | [6 empty] | 2 | [14 empty] | 2 | 1.2 | 2.4 | 807.96 | 1615.92
109 | Air Valve (15 mmØ) |  | no | [16 empty] | 4 |  |  |  | 20 | 1 | 20 | 2460 | 49200
110 | Air Valve (20 mmØ) |  | no | [16 empty] | 1 |  |  |  | 5 | 1.08 | 5.4 | 3135 | 15675
111 | HDPE Pipe (75 mmØ) |  | m | [5 empty] | 3 | [14 empty] | 3 | 0.9 | 2.7 | 215 | 645
112 | HDPE Pipe (90 mmØ) |  | m | [10 empty] | 20 | [9 empty] | 40 | 0.9 | 36 | 215 | 8600
113 | Float Valve (15 mmØ) |  | no | [20 empty] | 0 | 1.4 | 0 | 1300 | 0
114 | Float Valve (25 mmØ) |  | no | 6 | [19 empty] | 36 | 1.7 | 61.2 | 1800 | 64800
115 | End Cap (20 mmØ) |  | no | [20 empty] | 0 | 0.1 | 0 | 25 | 0
116 | End Cap (50 mmØ) |  | no | 6 |  | 2 | [17 empty] | 40 | 0.2 | 8 | 120 | 4800
117 | Brass bib Cock 15mm (250gm) |  | no | [20 empty] | 0 | 0.25 | 0 | 400 | 0
118 | Brass Bib Cock 15mm (400gm) |  | no | [11 empty] | 1 | [8 empty] | 1 | 0.4 | 0.4 | 795 | 795
| Total | [24 empty] | 1934.2501 |  | 990713.57
[26 empty] | VAT@13% |  | 128792.7641
[26 empty] | Total |  | 1119506.3341

## conp (hidden)
Shankharapur Municipality
Office of Municipal Executive
Sankhu, Kathmandu
Detail Estimated Sheet
Project:- Sankhu Khanepaani
Location:- Shankharapur Municipality-06,07
S.N. | Description of work | Quantity | Unit | Rate | Amount | Quantity | Amount | Difference | Remarks
1 | Earthworks in excavation in hard soil as per standard specification | 164.48 | m3 | 300 | 49344 | 80.4638 | 24139.1475 | -25204.8525
2 | Backfilling with Hard Soil as per standard specifications all complete | 63.95 | m3 | 80 | 5116 | 0 | 0 | -5116
3 | Dry Stone Soling in foundation in perfect line and level all complete | 45.68 | m3 | 4000 | 182720 | 27.0083 | 108033 | -74687
4 | Providing and laying of 1:2:4 PCC as per drawing and Standard specifications all complete | 25.69 | m3 | 9000 | 231210 | 15.5693 | 140123.25 | -91086.75
5 | Providing Plaster works 1:4 , 12.5mm with 3mm punning all complete as per standard specifications | 416.71 | m2 | 400 | 166684 | 22.2065 | 8882.6 | -157801.4
6 | Providing of Form work for concrete work in shear wall,etc as per standard norms and specifications all complete | 326.86 | m2 | 750 | 245145 | 323.2655 | 242449.125 | -2695.875
7 | PCC for RCC works in CSA 1:1.5:3 (ढलानको कार्य) with water proofing chemical all complete in water tank and slab cover | 212.13 | m3 | 12000 | 2545560 | 52.9155 | 634986.36 | -1910573.64
8 | Cutting , bending and laying of Reinforcement works FE-500 as per given drawing and standard specifications all complete | 9324.57 | kg | 105 | 979079.85 | 3508.7322 | 368416.8835 | -610662.9665
9 | Random Rubble Stone Masonry in C/S 1:4 including weep holes in perfect line and level with proper curing all complete. | 259.1 | m3 | 5000 | 1295500 | 97.8944 | 489471.75 | -806028.25
11 | Supply and fitting of Rectangular 24"x24" (50 kg) C.I. tank manhole Cover locking types for burkamala Intake | 2 | Nos | 5000 | 10000 | 2 | 10000 | 0
12 | Gabion Works: Gabion Preparation, mesh forming etc. (size 2mx1mx1m) | 48 | m3 | 2500 | 120000 | 38 | 95000 | -25000
13 | Gabion Works: Filling of gabion box with stones | 48 | m3 | 2500 | 120000 | 38 | 95000 | -25000
[5 empty] | 5950358.85 |  | 2216502.116 | -3733856.734
[5 empty] | 773546.6505 |  | 288145.2751
[5 empty] | 6723905.5005 |  | 2504647.3911
14 | Project Information Board | 1 | ps | 5000 | 5000 | 1 | 5000
15 | Lab Test Report | 1 | ps | 20000 | 20000 | 1 | 20000
16 | Insurance | 1 | ps | 20000 | 20000 | 1 | 20000
17 | Other necessary fittings as required on site | 1 | ps | 100000 | 100000 | 1 | 100000
| Total with VAT and PS |  |  |  | 6868905.5005 |  | 2649647.3911
| Contingencies 3% |  |  |  | 178510.7655 |  | 66495.0635
| Grand Total |  |  |  | 7047416.266 |  | 5365789.8457

## Sheet5 (hidden)
Shankharapur Municipality
Office of Municipal Executive
Sankhu, Kathmandu
First Running Bill
| योजनाको नामः | Sankhu Khanepani | [6 empty] | बिलको क्रम सङ्ख्याः |  | 1
| योजना कार्यान्वयन हुने स्थानः | shankharapur-6,7,4 | [6 empty] | कार्य आदेश मितिः |  | 2078-12-07
| ठेकदारको नामः | Consolidated Builders and Engineers Pvt. Ltd., lalitpur | [6 empty] | काम सम्पन्न गर्नु पर्ने मितिः |  | 2079-03-10
| ठेक्का पट्टाको सङ्केतः | SMO/078/79/56 | [6 empty] | म्याद थप/भेरिएसन मितिः
| नापी किताब नं | [7 empty] | काम सम्पन्न भएको मितिः |  | June 20 2022
Item.No | Description of work | Unit | सम्झौता बमोजिम |  |  | हाल भएको काम |  | अगिल्लो बिलमा भएको काम |  | हाल सम्म भएको काम |  | बाकि काम
|  |  | परिमाण | दर | रकम | परिमाण | रकम | परिमाण | रकम | परिमाण | रकम
1 | Earthworks in excavation in hard soil as per standard specification | m3 | 164.48 | 300 | 49344 | 80.4638 | 24139.1475 |  |  | 80.4638 | 24139.1475 | -84.0162
2 | Backfilling with Hard Soil as per standard specifications all complete | m3 | 63.95 | 80 | 5116 | 0 | 0 |  |  | 0 | 0 | -63.95
3 | Dry Stone Soling in foundation in perfect line and level all complete | m3 | 45.68 | 4000 | 182720 | 27.0083 | 108033 |  |  | 27.0083 | 108033 | -18.6717
4 | Providing and laying of 1:2:4 PCC as per drawing and Standard specifications all complete | m3 | 25.69 | 9000 | 231210 | 15.5693 | 140123.25 |  |  | 15.5693 | 140123.25 | -10.1207
5 | Providing Plaster works 1:4 , 12.5mm with 3mm punning all complete as per standard specifications | m2 | 416.71 | 400 | 166684 | 22.2065 | 8882.6 |  |  | 22.2065 | 8882.6 | -394.5035
6 | Providing of Form work for concrete work in shear wall,etc as per standard norms and specifications all complete | m2 | 326.86 | 750 | 245145 | 323.2655 | 242449.125 |  |  | 323.2655 | 242449.125 | -3.5945
7 | PCC for RCC works in CSA 1:1.5:3 (ढलानको कार्य) with water proofing chemical all complete in water tank and slab cover | m3 | 212.13 | 12000 | 2545560 | 52.9155 | 634986.36 |  |  | 52.9155 | 634986.36 | -159.2145
8 | Cutting , bending and laying of Reinforcement works FE-500 as per given drawing and standard specifications all complete | kg | 9324.57 | 105 | 979079.85 | 3508.7322 | 368416.8835 |  |  | 3508.7322 | 368416.8835 | -5815.8378
9 | Random Rubble Stone Masonry in C/S 1:4 including weep holes in perfect line and level with proper curing all complete. | m3 | 259.1 | 5000 | 1295500 | 97.8944 | 489471.75 |  |  | 97.8944 | 489471.75 | -161.2056
11 | Supply and fitting of Rectangular 24"x24" (50 kg) C.I. tank manhole Cover locking types for burkamala Intake | Nos | 2 | 5000 | 10000 | 2 | 10000 |  |  | 2 | 10000 | 0
12 | Gabion Works: Gabion Preparation, mesh forming etc. (size 2mx1mx1m) | m3 | 48 | 2500 | 120000 | 38 | 95000 |  |  | 38 | 95000 | -10
13 | Gabion Works: Filling of gabion box with stones | m3 | 48 | 2500 | 120000 | 38 | 95000 |  |  | 38 | 95000 | -10
| Total |  |  |  | 5950359 |  | 2216502.116 |  |  |  | 2216502.116 | 0
| 13 % VAT |  |  |  | 773546.67 |  | 288145.2751 |  |  |  | 288145.2751 | 0
|  | Total with VAT |  |  | 6723905.67 |  | 2504647.3911 |  |  |  | 2504647.3911 | 0
Provisional sum
14 | Project Information Board | ps | 1 | 5000 | 5000 | 1 | 5000 |  |  | 1 | 5000
15 | Lab Test Report | ps | 1 | 20000 | 20000 | 1 | 0 |  |  | 1 | 0
16 | Insurance | ps | 1 | 20000 | 20000 | 1 | 0 |  |  | 1 | 0
17 | Other necessary fittings as required on site | ps | 1 | 100000 | 100000 | 1 | 0 |  |  | 1 | 0
| Grand total Rs. |  |  |  | 6868905.67 |  | 2509647.3911 |  |  |  | 2509647.3911
उपर्युक्त बमोजिम ठीक छ भनी प्रमाणित गर्नेको सही ः–
| यो बमोजिमको जम्मा रु. |  | 2509647.3911 |  |  | भ्याट सहित |  |  | ङ) धरौटी @5% का दरले |  | 110825.1058
| अघिल्लो बिलबाट भुक्तानी भएको रु. |  | 0 |  |  | भ्याट सहित |  |  | च) अग्रीम आयकरः – 1.5% का दरले जम्मा रु.
| बाँकी दिनु पर्ने रु. |  | 2509647.3911 |  |  | भ्याट सहित |  |  | ठेकेदारको सही ः–
| कट्टा गर्नू पर्ने रु | [7 empty] | खुद दिनु पर्ने रु.
| क) पेश्की | [7 empty] | जम्मा रु: …………………..……...अक्षेरेपी...............को चेक नं
| नाप जाँच गर्नेको सही |  |  | चेक गर्नेको सही | [6 empty] | स्वीकृत गर्नेको सही

## Valuated abstract (hidden)
Shankharapur Municipality
Office of Municipal Executive
Sankhu, Kathmandu
Abstract of Valuated Cost
Bill No.: First Running Bill
Contractors Name: Consolidated Builders and Engineers Pvt. Ltd., lalitpur
Contract No.: SMO/078/79/51
Project:- Sankhu Khanepaani | [5 empty] | Date: 2079/03/09
Location:- Shankharapur Municipality-06,07
FY :78/79
S.N. | Description of work | Quantity | Unit | Rate | Amount | Remarks | ‍
1 | Earthworks in excavation in hard soil as per standard specification | 80.4638 | m3 | 300 | 24139.1475
2 | Backfilling with Hard Soil as per standard specifications all complete | 0 | m3 | 80 | 0
3 | Dry Stone Soling in foundation in perfect line and level all complete | 27.0083 | m3 | 4000 | 108033
4 | Providing and laying of 1:2:4 PCC as per drawing and Standard specifications all complete | 15.5693 | m3 | 9000 | 140123.25
5 | Providing Plaster works 1:4 , 12.5mm with 3mm punning all complete as per standard specifications | 22.2065 | m2 | 400 | 8882.6
6 | Providing of Form work for concrete work in shear wall,etc as per standard norms and specifications all complete | 323.2655 | m2 | 750 | 242449.125
7 | PCC for RCC works in CSA 1:1.5:3 (ढलानको कार्य) with water proofing chemical all complete in water tank and slab cover | 52.9155 | m3 | 12000 | 634986.36
8 | Cutting , bending and laying of Reinforcement works FE-500 as per given drawing and standard specifications all complete | 3508.7322 | kg | 105 | 368416.8835
9 | Random Rubble Stone Masonry in C/S 1:4 including weep holes in perfect line and level with proper curing all complete. | 97.8944 | m3 | 5000 | 489471.75
11 | Supply and fitting of Rectangular 24"x24" (50 kg) C.I. tank manhole Cover locking types for burkamala Intake | 2 | Nos | 5000 | 10000
12 | Gabion Works: Gabion Preparation, mesh forming etc. (size 2mx1mx1m) | 38 | m3 | 2500 | 95000
13 | Gabion Works: Filling of gabion box with stones | 38 | m3 | 2500 | 95000
|  |  |  | Sub Total | 2216502.116
|  |  |  | VAT 13% | 288145.2751
|  |  |  | Total | 2504647.3911
14 | Project Information Board | 1 | ps | 5000 | 5000
15 | Lab Test Report | 1 | ps |  | 0
16 | Insurance | 1 | ps |  | 0
17 | Other necessary fittings as required on site | 1 | ps |  | 0
|  |  |  | Total With VAT and PS | 2509647.3911
|  |  |  | Contingencies 3% | 66495.0635
|  |  |  | Grand Total | 2576142.4546 |  | 66979.7038

## Detail Measurement (hidden)
Shankharapur Municipality
Office of Municipal Executive
Sankhu, Kathmandu
Detail Measurement Sheet
Bill No.: First Running Bill
Contractors Name: Consolidated Builders and Engineers Pvt. Ltd., lalitpur
Contract No.: SMO/078/79/51
Project:- Sankhu Khanepaani | [9 empty] | Date: 2079/03/09
Location:- Shankharapur Municipality-06,07
FY :78/79
S.N. | Description of work | No. | Length | Breadth | Height | Quantity | Unit | Rate | Amount | Remarks | ‍
1 | Earthworks in excavation in hard soil
| RCC drain | 1 | 61.05 | 1.5 | 0.3 | 27.4725
| Retaining wall at boundary | 1 | 25.7 | 1.1 | 0.6 | 16.962
| Retaining wall near roughing filter | 1 | 29.6 | 0.75 | 0.6 | 13.32 |  |  |  | two step
|  | 1 | 4.35 | 0.75 | 0.3
| Retaining wall near the old intake | 1 | 2.8 | 0.7 | 0.6 | 1.176
|  | 1 | 1.4 | 0.6 | 0.6 | 0.504
|  | 1 | 1.5 | 0.7 | 0.6 | 0.63
| Burkamala intake |  |  |  |  | 20.3993
[6 empty] | 80.4638 | m3 | 1362.18 | 109606.2131
2 | Backfilling with Hard Soil
Behind retaining wall
[6 empty] | 0 | m3 | 686.54 | 0
3 | Stone Soling in foundation in perfect line and level all complete(जगमा ढुंगा भर्ने काम)
| RCC drain | 1 | 61.05 | 1.5 | 0.15 | 13.7363
| Retaining wall at boundary | 1 | 25.7 | 1.1 | 0.15 | 4.2405
| Retaining wall near roughing filter | 1 | 29.6 | 0.75 | 0.15 | 3.33
| Retaining wall near the old intake | 1 | 0 | 0.7 | 0.15 | 0
|  | 1 | 1.4 | 0.6 | 0.15 | 0.126
|  | 1 | 1.5 | 0.7 | 0.15 | 0.1575
| new Intake at burkamala |  |  |  |  | 5.418
[6 empty] | 27.0083 | m3 | 5141.87 | 138872.9104
4 | 1:2:4 PCC (पी. सी सी)
| RCC drain | 1 | 61.05 | 1.5 | 0.075 | 6.8681
| Retaining wall at boundary | 1 | 25.7 | 1.1 | 0.075 | 2.1203
|  | 1 | 25.7 | 0.6 | 0.05 | 0.771
| Retaining wall near roughing filter | 1 | 29.6 | 0.75 | 0.075 | 1.665
|  | 1 | 29.6 | 0.75 | 0.05 | 1.11
Retaining wall near the old intake
| burkamala Intake PCC |  |  |  |  | 3.0349
[6 empty] | 15.5693 | m3 | 15694.9 | 244357.8218
5 | Plaster works 1:4 प्लास्टरको काम 12.5mm with 3mm punning
| Burkamala Intake |  |  |  |  | 22.2065
[6 empty] | 22.2065 | m2 | 810.6 | 18000.5889
VAT
6 | Form work for concrete work in shear wall,etc
| RCC drain | 2 | 61.05 |  | 0.6 | 73.26
| shear wall | 3 | 61.05 |  | 0.91 | 166.6665
| burkamala intake |  |  |  |  | 83.339
[6 empty] | 323.2655 | m2 | 1278.27 | 413220.5907
7 | PCC for RCC works in CSA 1:1.5:3 (ढलानको कार्य) with water proofing chemical all complete in water tank and slab cover
RCC drain
| section 1 | 1 | 3 | 1.5 | 0.15 | 0.675
|  | 2 | 3 | 0.15 | 0.6 | 0.54
| section 2 | 1 | 9.8 | 1.5 | 0.15 | 2.205
|  | 2 | 9.8 | 0.15 | 0.6 | 1.764
| section 3 | 1 | 9.1 | 1.65 | 0.15 | 2.2522
|  | 2 | 9.1 | 0.15 | 0.6 | 1.638
| section 4 | 1 | 5.2 | 1.9 | 0.15 | 1.482
|  | 2 | 5.2 | 0.15 | 0.65 | 1.014
| section 5 | 1 | 2.5 | 2.45 | 0.15 | 0.91875
|  | 2 | 2.5 | 0.15 | 0.6 | 0.45
| section 6 | 1 | 5.8 | 2.6 | 0.15 | 2.262
|  | 2 | 5.8 | 0.15 | 0.6 | 1.044
| section 7 | 1 | 1.1 | 1.2 | 0.15 | 0.198
|  | 1 | 1.1 | 0.15 | 0.6 | 0.099
| section 8 | 1 | 1.2 | 1.2 | 0.15 | 0.216
|  | 2 | 1.2 | 0.15 | 0.9 | 0.324
| section 9 | 1 | 2.3 | 1.25 | 0.15 | 0.43125
|  | 2 | 2.3 | 0.15 | 0.6 | 0.414
| section 10 | 1 | 2.45 | 1.5 | 0.15 | 0.55125
|  | 2 | 2.45 | 0.15 | 0.65 | 0.47775
| section 11 | 1 | 11.7 | 0.65 | 0.15 | 1.1407
|  | 2 | 11.7 | 0.15 | 0.62 | 2.1762
| section 12 | 1 | 6.9 | 0.7 | 0.15 | 0.7245
|  | 2 | 6.9 | 0.15 | 0.65 | 1.3455
| Burkamala intake |  | 61.05 | 1.5083 |  | 28.5723
|  |  | ` |  | Total | 52.9155 | m3 | 16948.41 | 896834.0978
8 | Reinforcement works | Nos | Length(m) | Total Length(m) | kg/m | Total weight(kg)
RCC Drain
| 10 mm Ø circular | 408 | 3.65 | 0.62 | kg/m | 923.304
| 10 mm Ø stirrups @ 200mm c/c | 19 | 67.155 | 0.62 | kg/m | 791.0859
| Burkamala intake |  |  |  |  | 1794.3423
3508.7322
[6 empty] | 3508.7322 | kg | 123.56 | 433538.9536
9 | Random Rubble Stone Masonry in C/S 1:4 including weep holes in perfect line and level with proper curing all complete.
| Retaining wall at boundary | 1 | 25.7 | 0.85 | 2.43 | 53.0834
| Retaining wall near roughing filter | 1 | 29.6 | 0.75 | 1.35 | 29.97
|  | 1 | 4.35 | 0.75 | 1.2 | 3.915
| Check dam | 12 | 1.5 | 0.35 | 1 | 6.3
| Retaining wall near the intake | 1 | 2.8 | 0.6 | 1.4 | 2.352
|  | 1 | 1.4 | 0.6 | 1.1 | 0.924
|  | 1 | 1.5 | 0.6 | 1.5 | 1.35
[6 empty] | 97.8944 | m3 | 14084.92 | 1378834.0882
11 | Supply and fitting of Rectangular 24"x24" (50 kg) C.I. tank manhole Cover locking types for burkamala Intake | 2 |  |  |  | 2 | Nos | 10755 | 21510
12 | Gabion Works: Gabion Preparation, mesh forming etc. (size 2mx1mx1m) | 19 | 2 | 1 | 1 | 38 | m3 | 2649.54 | 100682.52
13 | Gabion Works: Filling of gabion box with stones |  |  |  |  | 38 | m3 | 3787.63 | 143929.94
[8 empty] | Sub Total | 3899387.7246
[8 empty] | VAT 13% | 506920.4042
[8 empty] | Total | 4406308.1288
14 | Project Information Board |  |  |  |  | 1 | ls | 5000 | 5000
15 | Lab Test Report |  |  |  |  | 1 | ls | 20000 | 20000
16 | Insurance |  |  |  |  | 1 | ls | 20000 | 20000
17 | Other necessary fittings as required on site |  |  |  |  | 1 | ps | 100000 | 100000
[8 empty] | Contingencies 3% | 116981.6317
[8 empty] | Grand Total | 4668289.7605 |  | 121375.5338

## Intake (v) (hidden)
Detail measurement Sheet
TYPE OF WORK : Intake-3 Construction works-Fedi
S.no. | Description of works | Unit | No. | Length,m | Breadth,m | Height,m | Quantity | Rate | Amount | Remarks
1 | Site Clearance
2 | Earthwork Excavation
| Collection tank and chamber |  | 1 | 4.17 | 2.45 | 1.05 | 10.7273 |  |  |  | 1.75 | 0.56
| Weir |  | 2 | 5.2 | 0.3 | 0.6 | 1.872
| Damn |  | 1 | 5.2 | 5 | 0.3 | 7.8
|  | Cum |  |  |  | Total | 20.3993
3 | Stone Soling
| under Collection tank& chamber |  | 1 | 4.4 | 2.3 | 0.15 | 1.518
| For Raft |  | 1 | 5.2 | 5 | 0.15 | 3.9
|  | Cum |  |  |  | Total | 5.418
4.1 | PCC M15
| under Collection tank& chamber |  | 1 | 4.4 | 2.3 | 0.075 | 0.759
| Weir |  | 2 | 5.2 | 0.3 | 0.075 | 0.234
| For Raft |  | 1 | 5.2 | 5 | 0.075 | 1.95
| shear wall |  | 1 | 3.5 | 0.35 | 0.075 | 0.091875
|  | Cum |  |  |  | Total | 3.0349
4.2 | RCC works M20
| Collection tank & chamber |  | 1 | 4.17 | 0.3 | 1.4 | 1.7514
|  |  | 1 | 3.8 | 0.3 | 1.4 | 1.596
| Short wall & Partition |  | 3 | 1.7 | 0.3 | 1.4 | 2.142
| Raft for tank & chamber |  | 1 | 3.985 | 2.46 | 0.3 | 2.9409
| Slab |  | 1 | 3.985 | 2.4 | 0.125 | 1.1955
| Parapet above tank |  | 1 | 4 | 0.3 | 0.2 | 0.24
| Weir |  | 2 | 5.2 | 0.3 | 0.6 | 1.872
| Raft For Damn |  | 1 | 5.2 | 5 | 0.3 | 7.8
| shear wall |  | 1 | 3.5 | 0.3 | 2.1 | 2.205
| damn Part-1 |  | 1 | 5.3 | 0.9 | 1.1 | 5.247
| damn Part-2 |  | 1 | 1.7 | 0.75 | 0.8 | 1.02
|  |  | 1 | 1.25 | 0.3 | 1.5 | 0.5625
|  | Cum |  |  |  | Total | 28.5723
6 | Form Works
| Collection tank & chamber |  | 2 | 4.17 |  | 1.4 | 11.676
|  |  | 2 | 3.8 |  | 1.4 | 10.64
| Short wall & Partition |  | 6 | 1.7 |  | 1.4 | 14.28
| Raft for tank & chamber |  | 1 | 12.73 |  | 0.3 | 3.819
| Slab |  | 1 | 3.985 | 2.4 |  | 9.564
| Parapet above tank |  | 2 | 4 |  | 0.2 | 1.6
| Raft For Damn |  | 1 | 20.4 |  | 0.3 | 6.12
| shear wall |  | 2 | 3.5 |  | 2.1 | 14.7
| damn Part-1 |  | 1 | 5.3 |  | 1.1 | 5.83
| damn Part-2 |  | 1 | 1.7 |  | 0.8 | 1.36
| Shear wall (Slope) |  | 2 | 1.25 |  | 1.5 | 3.75
|  | sqm |  |  |  | Total | 83.339
7 | Reinforcement | kg |  |  |  |  | 1794.3423
10 | Cement punning
| Collection Chamber | sqm | 1 | 2.5 | 1.5 |  | 3.75
| Wall | sqm | 2 | 8 |  | 2.15 | 34.4
| Valve Chamber | sqm | 1 | 1.5 | 1 |  | 1.5
| Wall | sqm | 2 | 5 |  | 0.8 | 8
|  | sqm |  |  |  | Total | 47.65
11 | 12.5 mm thick cement plaster on concrete surface with 1:3 cement sand mortar
|  |  | 2 | 2.15 |  | 1.4 | 6.02
|  |  | 2 | 3.27 |  | 1.4 | 9.156
|  |  | 1 | 2.15 | 3.27 |  | 7.0305
|  | sqm |  |  |  | Total | 22.2065
12 | Gabion Works
Gabion Rip Rap Mesh
| 2mx1mx1m | Cum | 19 | 2 | 1 | 1 | 38
13 | 600dia. Manhole Cover | No. | 2 |  |  |  | 2
15 | Supplying and laying Pipes Fittings
| 75∅ Tee | No. | 2 |  |  |  | 2
| 75∅ Elbow | No. | 2 |  |  |  | 2
| 75∅ Pipe Piece | No. | 10 |  |  |  | 10
| 65∅ Gate Valve | No. | 2 |  |  |  | 2
| 65∅ Union | No. | 2 |  |  |  | 2
| 65∅ Nipple | No. | 2 |  |  |  | 2
| 65/75 GI/PE Flanged set | No. | 2 |  |  |  | 2
| 75∅ PE Stainer | No. | 1 |  |  |  | 1
TYPE OF WORK : Boulder Pitching in river
S.no. | Description of works | Unit | No. | Length,m | Breadth,m | Height,m | Quantity |  |  | Remarks
1 | Earthwork Excavation
|  | cum | 1 | 50 | 2.68 | 1 | 134
|  | cum |  |  |  |  | 134
2 | Back filling
|  | cum | 1 | 25 | 1.2 | 1 | 30
|  | cum |  |  |  |  | 30
4 | Masonary Works
4.1 | Stone Soling | cum | 1 | 50 | 1.68 | 0.2 | 16.8
|  | cum |  |  |  |  | 16.8
4.3 | Stone Masonary(1:6)
|  | cum | 1 | 50 | 0.35 | 0.32 | 5.6 |  |  |  | 2.1335 | 4.9215
| Gate Pillar | cum | 2 | 0.45 | 0.45 | 1.5 | 0.61
|  | cum |  |  |  |  | 6.21
5 | P.C.C Works
M10
|  | cum | 1 | 50 | 1.68 | 0.1 | 8.4
| In MS Posts Casting (Bottom) | cum | 28 | 0.13 | 0.13 | 0.05 | 0.02
| In MS Posts Casting (Side) | cum | 28 | 0.13 | 0.035 | 0.26 | 0.03
|  | cum |  |  |  |  | 8.45
M15
| Wall Coping | cum | 1 | 50 | 0.35 | 0.05 | 0.88
|  | cum |  |  |  |  | 0.88
6 | Formworks
|  | sqm | 2 | 51.68 |  | 0.1 | 10.34
| Wall Coping | sqm | 2 | 50.35 |  | 0.05 | 5.04
|  | sqm |  |  |  |  | 15.38
7 | 12.5mm thick c/s plaster (1:4) in wall (both sides) and 100mm below GL
|  | sqm | 2 | 0.13 |  | 0.495 | 0.13
|  | sqm |  |  |  |  | 0.13
8 | Fencing by galvanised chain link of 10SWG with 50mm bore MS pipe (@2m c/c), 25x25x4 mm MS angle & 100 mm long 3x20mm MS strip
|  | sqm | 1 | 0.13 |  | 1.78 | 0.23
|  | sqm |  |  |  |  | 0.23
9 | Gabion Works
| 2x1x1 | cum | 16 | 2 | 1 | 1 | 32
|  | cum |  |  |  |  | 32

## ABSTRACT (hidden)
Shankharapur Municipality
Office of Municipal Executive
Sankhu, Kathmandu
Detail Estimated Sheet
Project:- Sankhu Khanepaani
Location:- Shankharapur Municipality-06,07
FY :78/79
S.N. | Description of work | Quantity | Unit | Rate | Amount | Remarks | ‍
1 | Earthworks in excavation in hard soil as per standard specification | 164.476 | m3 | 1362.18 | 224045.9841
2 | Backfilling with Hard Soil as per standard specifications all complete | 63.95 | m3 | 686.54 | 43904.233
3 | Dry Stone Soling in foundation in perfect line and level all complete | 45.6844 | m3 | 5141.87 | 234903.133
4 | Providing and laying of 1:2:4 PCC as per drawing and Standard specifications all complete | 25.6907 | m3 | 15694.9 | 403212.7952
5 | Providing Plaster works 1:4 , 12.5mm with 3mm punning all complete as per standard specifications | 416.715 | m2 | 810.6 | 337789.179
6 | Providing of Form work for concrete work in shear wall,etc as per standard norms and specifications all complete | 326.86 | m2 | 1278.27 | 417815.3322
7 | PCC for RCC works in CSA 1:1.5:3 (ढलानको कार्य) with water proofing chemical all complete in water tank and slab cover | 212.1267 | m3 | 16948.41 | 3595209.9776
8 | Cutting , bending and laying of Reinforcement works FE-500 as per given drawing and standard specifications all complete | 9324.5713 | kg | 123.56 | 1152144.0339
9 | Random Rubble Stone Masonry in C/S 1:4 including weep holes in perfect line and level with proper curing all complete. | 259.099 | m3 | 14084.92 | 3649388.6871
11 | Supply and fitting of Rectangular 24"x24" (50 kg) C.I. tank manhole Cover locking types for burkamala Intake | 2 | Nos | 10755 | 21510
12 | Gabion Works: Gabion Preparation, mesh forming etc. (size 2mx1mx1m) | 48 | m3 | 2649.54 | 127177.92
13 | Gabion Works: Filling of gabion box with stones | 48 | m3 | 3787.63 | 181806.24
|  |  |  | Sub Total | 10388907.5151
|  |  |  | VAT 13% | 1350557.977
|  |  |  | Total | 11739465.4921
14 | Project Information Board | 1 | ps | 5000 | 5000
15 | Lab Test Report | 1 | ps | 20000 | 20000
16 | Insurance | 1 | ps | 20000 | 20000
17 | Other necessary fittings as required on site | 1 | ps | 100000 | 100000
|  |  |  | Contingencies 3% | 311667.2255
|  |  |  | Grand Total | 12196132.7176 |  | 317099.4507

## Estimate (hidden)
Shankharapur Municipality
Office of Municipal Executive
Sankhu, Kathmandu
Detail Estimated Sheet
Project:- Sankhu Khanepaani
Location:- Shankharapur Municipality-06,07
FY :78/79
S.N. | Description of work | No. | Length | Breadth | Height | Quantity | Unit | Rate | Amount | Remarks | ‍
1 | Earthworks in excavation in hard soil
| RCC drain | 1 | 74 | 1.8293 | 0.35 | 47.378
| Retaining wall at boundary | 1 | 37.5 | 1 | 0.6 | 22.5
| Retaining wall near roughing filter | 1 | 26.45 | 1.4 | 0.6 | 22.218
| Retaining wall near the old intake | 1 | 18 | 1.8 | 0.6 | 19.44
| Burkamala intake |  |  |  |  | 52.94
[6 empty] | 164.476 | m3 | 1362.18 | 224045.9841
2 | Backfilling with Hard Soil
| Behind retaining wall | 1 | 63.95 | 1 | 1 | 63.95
[6 empty] | 63.95 | m3 | 686.54 | 43904.233
3 | Stone Soling in foundation in perfect line and level all complete(जगमा ढुंगा भर्ने काम)
| RCC drain | 1 | 74 | 1.8293 | 0.15 | 20.3049
| Retaining wall at boundary | 1 | 37.5 | 1 | 0.15 | 5.625
| Retaining wall near roughing filter | 1 | 26.45 | 1.4 | 0.15 | 5.5545
| Retaining wall near the old intake | 1 | 18 | 1.8 | 0.15 | 4.86
| new Intake at burkamala |  |  |  |  | 9.34
[6 empty] | 45.6844 | m3 | 5141.87 | 234903.133
4 | 1:2:4 PCC (पी. सी सी)
| RCC drain | 1 | 74 | 1.8293 | 0.075 | 10.1524
| Retaining wall at boundary | 1 | 37.5 | 1 | 0.075 | 2.8125
|  | 1 | 37.5 | 0.6 | 0.05 | 1.125
| Retaining wall near roughing filter | 1 | 26.45 | 1.4 | 0.075 | 2.7772
|  | 1 | 26.45 | 0.6 | 0.05 | 0.7935
| Retaining wall near the old intake | 1 | 18 | 1.8 | 0.075 | 2.43
|  | 1 | 18 | 0.6 | 0.05 | 0.54
| burkamala Intake PCC |  |  |  |  | 5.06
[6 empty] | 25.6907 | m3 | 15694.9 | 403212.7952
5 | Plaster works 1:4 प्लास्टरको काम 12.5mm with 3mm punning
| RCC drain | 1 | 74 | 3.65 | 1.25 | 337.625
| Burkamala Intake |  |  |  |  | 79.09
[6 empty] | 416.715 | m2 | 810.6 | 337789.179
VAT
6 | Form work for concrete work in shear wall,etc
RCC drain
| shear wall | 3 | 74 |  | 0.91 | 202.02
| burkamala intake |  |  |  |  | 124.84
[6 empty] | 326.86 | m2 | 1278.27 | 417815.3322
7 | PCC for RCC works in CSA 1:1.5:3 (ढलानको कार्य) with water proofing chemical all complete in water tank and slab cover
RCC drain
| Base | 2 | 74 | 1.8293 | 0.417 | 112.8951
| Shear wall | 2 | 74 | 0.417 | 0.91 | 56.1616
| Burkamala intake |  |  |  |  | 43.07
|  |  | ` |  | Total | 212.1267 | m3 | 16948.41 | 3595209.9776
8 | Reinforcement works | Nos | Length(m) | Total Length(m) | kg/m | Total weight(kg)
RCC Drain
| 12 mm Ø circular | 494.3333 | 3.65 | 0.89 | kg/m | 1605.8418
| 8 mm Ø stirrups @ 200mm c/c | 19 | 81.4 | 0.4 | kg/m | 618.64
| Burkamala intake |  |  |  |  | 7100.0895
9324.5713
[6 empty] | 9324.5713 | kg | 123.56 | 1152144.0339
9 | Random Rubble Stone Masonry in C/S 1:4 including weep holes in perfect line and level with proper curing all complete.
| Retaining wall at boundary | 1 | 37.5 | 0.8 | 2.5 | 75
| Retaining wall near roughing filter | 1 | 26.45 | 1 | 3.5 | 92.575
| Check dam | 8 | 1.83 | 0.35 | 1 | 5.124
| Retaining wall near the intake | 1 | 18 | 1.2 | 4 | 86.4
[6 empty] | 259.099 | m3 | 14084.92 | 3649388.6871
11 | Supply and fitting of Rectangular 24"x24" (50 kg) C.I. tank manhole Cover locking types for burkamala Intake | 2 |  |  |  | 2 | Nos | 10755 | 21510
12 | Gabion Works: Gabion Preparation, mesh forming etc. (size 2mx1mx1m) | 24 | 2 | 1 | 1 | 48 | m3 | 2649.54 | 127177.92
13 | Gabion Works: Filling of gabion box with stones |  |  |  |  | 48 | m3 | 3787.63 | 181806.24
[8 empty] | Sub Total | 10388907.5151
[8 empty] | VAT 13% | 1350557.977
[8 empty] | Total | 11739465.4921
14 | Project Information Board |  |  |  |  | 1 | ls | 5000 | 5000
15 | Lab Test Report |  |  |  |  | 1 | ls | 20000 | 20000
16 | Insurance |  |  |  |  | 1 | ls | 20000 | 20000
17 | Other necessary fittings as required on site |  |  |  |  | 1 | ps | 100000 | 100000
[8 empty] | Contingencies 3% | 311667.2255
[8 empty] | Grand Total | 12196132.7176 |  | 317099.4507

## Intake (hidden)
QUANTITY ESTIMATE
TYPE OF WORK : Intake-3 Construction works-Fedi
S.no. | Description of works | Unit | No. | Length,m | Breadth,m | Height,m | Quantity | Rate | Amount | Remarks
1 | Site Clearance | sqm | 1 | 9 | 21.3 |  | 191.7
2 | Earthwork Excavation
| RCC Weir | Cum | 1 | 6 | 0.3 | 1.525 | 2.75 |  |  |  | 1.75 | 0.56
|  | Cum | 1 | 6 | 1.7 | 0.525 | 5.36
|  | Cum | 1 | 6 | 0.3 | 1.525 | 2.75
|  | Cum | 1 | 6 | 3 | 0.525 | 9.45
| Collection and Valve Chamber | Cum | 1 | 2.1 | 4.35 | 1.8 | 16.44
| wall | cum | 1 | 8.3 | 1.3 | 1.5 | 16.19
|  | Cum |  |  |  | Total | 52.94
3 | Stone Soling
| RCC Weir | Cum | 1 | 6 | 5.3 | 0.15 | 4.77
|  |  | 1 | 7.3 | 1.3 | 0.15 | 1.42
| Collection and Valve Chamber | Cum | 1 | 2.1 | 4.85 | 0.15 | 1.53
| wall | cum | 1 | 8.3 | 1.3 | 0.15 | 1.62
|  | Cum |  |  |  | Total | 9.34
4.1 | PCC M15
| RCC Weir | Cum | 1 | 6 | 5.3 | 0.075 | 2.39
|  | Cum | 1 | 7.3 | 1.3 | 0.075 | 0.71
| Collection and Valve Chamber | Cum | 1 | 2.1 | 4.85 | 0.075 | 0.76
| wall | cum | 1 | 8.3 | 1.3 | 0.075 | 0.81
| Collection Chamber | sqm | 1 | 2.5 | 1.5 | 0.075 | 0.28
| Valve Chamber | sqm | 1 | 1.5 | 1 | 0.075 | 0.11
|  | Cum |  |  |  | Total | 5.06
4.2 | RCC works M20
| RCC Weir Wall | cum | 1 | 8 | 0.3 | 1.53 | 3.67
|  | cum | 1 | 8 | 1.7 | 0.3 | 4.08
|  | cum | 1 | 6 | 0.3 | 2.295 | 4.13
|  | cum | 1 | 6 | 3 | 0.3 | 5.4
|  | cum | 0.5 | 6 | 1.75 | 1 | 5.25
| Collection Chamber | cum | 1 | 2.1 | 4.85 | 0.3 | 3.06
|  | cum | 2 | 2.1 | 0.3 | 2.15 | 2.71
| Wall | cum | 2 | 4.345 | 0.3 | 2.15 | 5.61
| Cover slab | cum | 1 | 2.1 | 3.1 | 0.15 | 0.98
Valve Chamber
| Wall | cum | 1 | 4.6 | 0.25 | 2.15 | 2.47
| Cover slab | cum | 1 | 2.1 | 1.25 | 0.15 | 0.39
| Deduction of Manhole Cover | cum | -2 | 0.2826 | 0.3 | 0.15 | -0.03
| side Wall | cum | 1 | 8.3 | 0.3 | 2.15 | 5.35
|  | Cum |  |  |  | Total | 43.07
6 | Form Works
| RCC Weir Base | sqm | 1 | 22.6 |  | 0.075 | 1.7
| RCC Weir Wall | sqm | 1 | 16.6 |  | 1.53 | 25.4
|  | sqm | 1 | 19.4 |  | 0.3 | 5.82
|  | sqm | 1 | 12.6 |  | 2.295 | 28.92
|  | sqm | 1 | 12 |  | 0.3 | 3.6
| Collection Chamber | sqm | 2 | 13.9 |  | 0.3 | 8.34
| Wall | sqm | 1 | 9.29 |  | 2.15 | 19.97
| Cover slab | sqm | 1 | 2.4 | 3.4 |  | 8.16
Valve Chamber
| Wall | sqm | 2 | 4.6 |  | 2.15 | 19.78
| Cover slab | sqm | 1 | 2.4 | 1.55 |  | 3.72
| Deduction of Manhole Cover | sqm | -2 | 0.2826 |  |  | -0.57
|  | sqm |  |  |  | Total | 124.84
7 | Reinforcement | kg |  |  |  |  | 7100.0895
10 | Cement punning
| Collection Chamber | sqm | 1 | 2.5 | 1.5 |  | 3.75
| Wall | sqm | 2 | 8 |  | 2.15 | 34.4
| Valve Chamber | sqm | 1 | 1.5 | 1 |  | 1.5
| Wall | sqm | 2 | 5 |  | 2.15 | 21.5
|  | sqm |  |  |  | Total | 61.15
11 | 12.5 mm thick cement plaster on concrete surface with 1:3 cement sand mortar
Collection Chamber
| Wall | sqm | 2 | 8 |  | 2.15 | 34.4
| Cover slab | sqm | 2 | 2.4 | 3.4 |  | 16.32
Valve Chamber
| Wall | sqm | 2 | 5 |  | 2.15 | 21.5
| Cover slab | sqm | 2 | 2.4 | 1.55 |  | 7.44
| Deduction of Manhole Cover | sqm | -2 | 0.2826 |  |  | -0.57
|  | sqm |  |  |  | Total | 79.09
12 | Gabion Works
Gabion Rip Rap Mesh
| 2mx1mx1m | Cum | 1 | 14 | 10.6 | 0.3 | 44.52
13 | 600dia. Manhole Cover | No. | 2 |  |  |  | 2
15 | Supplying and laying Pipes Fittings
| 75∅ Tee | No. | 2 |  |  |  | 2
| 75∅ Elbow | No. | 2 |  |  |  | 2
| 75∅ Pipe Piece | No. | 10 |  |  |  | 10
| 65∅ Gate Valve | No. | 2 |  |  |  | 2
| 65∅ Union | No. | 2 |  |  |  | 2
| 65∅ Nipple | No. | 2 |  |  |  | 2
| 65/75 GI/PE Flanged set | No. | 2 |  |  |  | 2
| 75∅ PE Stainer | No. | 1 |  |  |  | 1
TYPE OF WORK : Boulder Pitching in river
S.no. | Description of works | Unit | No. | Length,m | Breadth,m | Height,m | Quantity |  |  | Remarks
1 | Earthwork Excavation
|  | cum | 1 | 50 | 2.68 | 1 | 134
|  | cum |  |  |  |  | 134
2 | Back filling
|  | cum | 1 | 25 | 1.2 | 1 | 30
|  | cum |  |  |  |  | 30
4 | Masonary Works
4.1 | Stone Soling | cum | 1 | 50 | 1.68 | 0.2 | 16.8
|  | cum |  |  |  |  | 16.8
4.3 | Stone Masonary(1:6)
|  | cum | 1 | 50 | 0.35 | 0.32 | 5.6 |  |  |  | 2.1335 | 4.9215
| Gate Pillar | cum | 2 | 0.45 | 0.45 | 1.5 | 0.61
|  | cum |  |  |  |  | 6.21
5 | P.C.C Works
M10
|  | cum | 1 | 50 | 1.68 | 0.1 | 8.4
| In MS Posts Casting (Bottom) | cum | 28 | 0.13 | 0.13 | 0.05 | 0.02
| In MS Posts Casting (Side) | cum | 28 | 0.13 | 0.035 | 0.26 | 0.03
|  | cum |  |  |  |  | 8.45
M15
| Wall Coping | cum | 1 | 50 | 0.35 | 0.05 | 0.88
|  | cum |  |  |  |  | 0.88
6 | Formworks
|  | sqm | 2 | 51.68 |  | 0.1 | 10.34
| Wall Coping | sqm | 2 | 50.35 |  | 0.05 | 5.04
|  | sqm |  |  |  |  | 15.38
7 | 12.5mm thick c/s plaster (1:4) in wall (both sides) and 100mm below GL
|  | sqm | 2 | 0.13 |  | 0.495 | 0.13
|  | sqm |  |  |  |  | 0.13
8 | Fencing by galvanised chain link of 10SWG with 50mm bore MS pipe (@2m c/c), 25x25x4 mm MS angle & 100 mm long 3x20mm MS strip
|  | sqm | 1 | 0.13 |  | 1.78 | 0.23
|  | sqm |  |  |  |  | 0.23
9 | Gabion Works
| 2x1x1 | cum | 16 | 2 | 1 | 1 | 32
|  | cum |  |  |  |  | 32

## Transp_1
Analysis of Transportation Cost (…………….)
Transportation Cost non Local materials
|  |  | Sector |  | Dist. | Dist. | Convenient |  | Inconvenient
S.N. | Mode of Transport |  |  |  | in | in | Rate/kg | Amount | Rate/kg | Amount
|  |  | From | To |  |  | /km/kosh |  | /km/kosh
[5 empty] | kosh | km | Rs. | Rs. | Rs. | Rs.
1 | Vehicle | Black Top
Gravel
Earthen
2 | Manual | Foot Trail | Roadhead | Site ( Av.) | 0 | 0 | 0.9 | 0 | 1.1 | 0
|  |  |  | Total |  |  |  | 0 |  | 0
Transportation cost per kg for convenient and inconvinient loads are fixed by the district for different
kinds of roads and manual transportation
Transportation Cost of Filter Media | [8 empty] | Transportation Cost of Sand
Quarry site: …………….. Khola | [8 empty] | Quarry site: ………………... Khola
|  |  | Sector |  | Dist. | Dist. | Convenient |  | Sector |  | Dist. | Dist. | Convenient
S.N. | Mode of Transport |  |  |  | in | in | Rate/kg | Amount |  |  | in | in | Rate/kg | Amount
|  |  | From | To |  |  | /km/kosh |  | From | To |  |  | /km/kosh
[5 empty] | kosh | km | Rs. | Rs. |  |  | kosh | km | Rs. | Rs.
1 | Vehicle | Black Top | highway | Pr. Site |  | 0 | 0.015 | 0 | highway | Pr. Site |  | 0 | 0.015 | 0
|  | Gravel | Quarry | highway |  | 0 | 0.015 | 0 | Quarry | highway |  | 0 | 0.015 | 0
Earthen
2 | Manual | Foot Trail | Porter | Site ( Av.) |  |  | 0.9 | 0 | Porter | Site ( Av.) |  |  | 0.9 | 0
|  |  |  | Total |  |  |  | 0 |  | Total |  |  |  | 0
Transportation Cost of Stones | [8 empty] | Transportation Cost of pipe and fittings
Quarry site: Nearby Quarry
|  |  | Sector |  | Dist. | Dist. | Convenient |  | Sector |  | Dist. | Dist. | Inconvenient
S.N. | Mode of Transport |  |  |  | in | in | Rate/kg | Amount |  |  | in | in | Rate/kg | Amount
|  |  | From | To |  |  | /km/kosh |  | From | To |  |  | /km/kosh
[5 empty] | kosh | km | Rs. | Rs. |  |  | kosh | km | Rs. | Rs.
1 | Vehicle | Black Top
Gravel
Earthen
2 | Manual | Foot Trail | Porter | Site ( Av.) | 0 |  | 1.1 | 0 | Porter | Site ( Av.) | 0 |  | 1.1 | 0
|  |  |  | Total |  |  |  | 0 |  | Total |  |  |  | 0

## Entry for Rates
FY
| For Analysis of Rates | [7 empty] | 081/82
| Name of Project : |  |  |  | Sankhu Drinking Water Supply Project
1 | For distance for transportation of non local materials
| Name of market |  |  |  | Sankhu
| Name of roadhead: |  |  |  | Sankhu |  |  |  | 984
Distance of project site from market on :
| - Earthen road |  |  | = | 0 | km
| - Gravel road |  |  | = | 0 | km
| - Metalled road |  |  | = |  | km
| - Foot |  |  | = | 0 | [5 empty] | 7.5
2 | For sand collection
| Sand is available in |  |  |  | Sankhu
| Mode of transportation of sand | [9 empty] | 1 | cft | 0.0283 | CuM | 1800
2.1 | If head load is there specify haul distance |  |  | = |  | km |  |  |  |  | 35.314 | cft | 0.99939 | CuM | 63565.2
2.2 | If there is tractor/ truck road specify distance
| - Earthen road |  |  | = | 0 | km
| - Gravel road |  |  | = | 0 | km
| - Metalled road |  |  | = |  | km
iii | If sand is to be purchased, specify cost/m3 |  |  |  | 3175.8797 | Rs/m3
3 | Collection of stone
| Distance of quarry from site |  |  |  | 0 | km
| If stone is to be purchased, specify cost/m3 |  |  |  | 2575.9913 | Rs/m3
4 | Aggregates
| If aggregate is to be purchased, specify cost/m3 |  |  |  | 3352.3174 | Rs/m3
5 | Local wood
5.1 | If it is obtained from sawing,
| specify distance of its availability |  |  |  |  | kosh
5.2 | If it is to be purchased, specify cost/m3 |  |  |  | 57400 | Rs/m3
6 | Salwood
6.1 | If it is obtained from sawing,
| specify distance of its availability |  |  |  | 0 | kosh
6.2 | If it is to be purchased, specify cost/m3 |  |  |  | 214901.1917 | Rs/m3
6 | Approved District Rates for transportatiopn and labours:
6.1 | District rate of transportation by head load for :
|  |  | - convenient load |  | 1.6 | Rs./kg.kosh
|  |  | - inconvenient load as bars, ms angle, etc. |  | 2.72 | Rs./kg.kosh
|  |  | - GI & HDPE pipes |  | 3.2 | Rs./kg.kosh
6.2 | If there no approved district rate for transportation by truck, and it is to be analyse
| Please click here, | Truck analysis | Truck analysis
6.3 | District rate of transportation by truck for convenient load on :
| - Earthen road |  | = |  | 6 | Rs./km.quintal
| - Gravel road |  | = |  | 3 | Rs./km.quintal
| - Metalled road |  | = |  | 1.75 | Rs./km.quintal
6.4 | District rate of transportation by truck for inconvenient load on :
| - Earthen road |  | = |  | 9 | Rs./km.quintal
| - Gravel road |  | = |  | 4.5 | Rs./km.quintal
| - Metalled road |  | = |  | 2.63 | Rs./km.quintal
6.5 | Rate of load / unload |  | = |  | 21.5 | Rs./quintal
6.6 | District rates of labours
| Rate of skilled labour |  |  |  | 1225 | Rs./day
| Rate of unskilled labour |  |  |  | 920 | Rs./day
| Rate of plumber |  |  |  | 1225 | Rs./day
| Helper |  |  |  | 920 | Rs./day
| Driver |  |  |  | 920 | Rs./day
| Asistant to driver |  |  |  | 810 | Rs./day
7 | Approved rate of nonlocal materials
Rate/ unit
7.1 |  |  | Cement, bag |  | 585 | Rs.
7.2 |  |  | Tor steel bars, kg |  | 90 | Rs.
7.3 |  |  | Binding wire, kg |  | 120 | Rs.
7.4 |  |  | Comercial GI plain wire, kg |  | 124 | Rs.
7.5 |  |  | Nails, kg |  | 132 | Rs.
7.6 |  |  | Chicken wire, m2 |  | 86 | Rs.
7.7 |  |  | Fly proof net, m² |  | 137 | Rs.
7.8 |  |  | M.S. Angle, kg |  | 93 | Rs.
7.9 |  |  | Barbed wire ( 12 SWG ), kg |  | 115 | Rs.
8 |  |  | GI Plain Sheet ( 26 SWG ), m2 |  | 462.7057 | Rs. | 462.7057
7.1 |  |  | CGI Sheet (26 SWG ), m2 |  | 470.6286 | Rs. | 17.5 m² = 1 bundle
7.11 |  |  | GI Plain Sheet for ridge cover, m |  | 244.96
7.12 |  |  | Primer, L |  | 288 | Rs.
7.13 |  |  | Enamel paint, L |  | 534 | Rs.
7.14 |  |  | Bitumen paint, kg |  | 249.73 | Rs. | 470.6286
7.15 |  |  | Snowcem paint, kg |  | 69 | Rs.
7.16 |  |  | Polythene sheet, m2 |  | 33 | Rs.
7.17 |  |  | Water proofing compound, kg |  | 117 | Rs.
7.18 |  |  | Fuel (Petrol), L |  | 147.79 | Rs.
7.19 |  |  | Holdfast, no |  | 21.14 | Rs. | 148 per kg
7.2 |  |  | Screw, no |  | 2 | Rs. | 80 per box
7.21 |  |  | Hinge 150 mm , no |  | 59 | Rs.
7.22 |  |  | Tower bolt 150mm , no |  | 71 | Rs.
7.23 |  |  | Tower bolt 300mm, no |  | 114 | Rs.
7.24 |  |  | Lockset 250 mm, no |  | 277 | Rs.
7.25 |  |  | Handle, no |  | 159 | Rs.
7.26 |  |  | Nut & Bolts, no |  | 12.18 | Rs. | 16 no/kg
7.27 |  |  | J-Hook, no |  | 17.125 | Rs. | 10 no/kg
7.28 |  |  | U-Hook, no |  | 17.125 | Rs.
7.29 |  |  | Bitumen Washer, no |  | 3 | Rs.
7.3 |  |  | Water seal pan, set |  | 0 | Rs.
7.31 |  |  | MS angle grill gate, of 12 kg |  | 1500 | Rs.
7.32 |  |  | MS angle manhole cover 60×60cm, set | 19.75kg | 2133 | Rs.
|  |  | MS angle manhole cover 60 cmØ, set | 13.7 kg | 1479.6 | Rs.
7.33 |  |  | MS angle manhole cover 45×45cm, set | 15.05 kg | 1625.4 | Rs.
7.34 |  |  | Suspender cable, 10 mmf, kg |  | 210.69 | Rs.
7.35 |  |  | Suspender cable, 14 mmf, kg |  | 268.15 | Rs.
7.36 |  |  | Bamboo, no |  | 240 | Rs.
7.37 |  |  | District rate of sawing per cft. |  |  | Rs.
7.38 |  |  | Royalty per cft |  |  | Rs.
7.39 |  |  | Mud per m³ |  | 343 | Rs.
7.4 |  |  | Tools and plant for pipe jointing, day |  | 500 | Rs.
If transportation cost is to be analysed, enter data here
7.41 |  |  | Cost of truck ( including VAT ) |  | 3164000 | Rs.
7.42 |  |  | Cost of tyre including VAT |  | 22400.25 | Rs.
7.43 |  |  | Salary of driver |  | 500 | Rs.
7.44 |  |  | Salary of asistant |  | 300 | Rs.
7.45 |  |  | H.S.D.,L |  | 65 | Rs.
7.46 |  |  | Mobil ,L |  | 580.26 | Rs.
7.47 |  |  | Gear oil ,L |  | 580.26 | Rs.
7.48 |  |  | Grease,L |  | 640.15 | Rs.
8 | Current Rate of Value Added Tax |  |  |  | 13
9 | Installation of pipes and fitings for spring intake, job |  |  |  | 600
9.1 | Installation of pipes and fitings for stream intake, job |  |  |  | 600
9.2 | Installation of pipes and fitings for ferrocement RVT, job |  |  |  | 1500
9.3 | Installation of pipes and fitings for collection chamber, job |  |  |  | 800
9.4 | Installation of pipes and fitings for distribution chamber, job |  |  |  | 800
9.5 | Installation of pipes and fitings for break pressure chamber, job |  |  |  | 800
9.6 | Installation of pipes and fitings for air valve chamber, job |  |  |  | 600
9.7 | Installation of pipes and fitings for valve chamber, job |  |  |  | 800
9.8 | Installation of pipes and fitings for public tap stand post, job |  |  |  | 600
9.9 | Installation of pipes and fitings for stream crossingt, job |  |  |  | 800
9.1 | Installation of pipes and fitings for cable crossingt, job |  |  |  | 1500
9.11 | Water diversion works in bed crossing, job |  |  |  | 1500
10 | Dewatering work in intake works, job |  |  |  | 450
PipeCost (GI Heavy Duty)
| Diameter of pipe | Unit | Pipe(Pg 64) | Tee (Pg 65) | Gate Valve | Check Valve | Elbow | Union | Socket | CI Plug | Hex Nipple | Re. Tee | Re. Elbow | Re Socket | Short bend | Cross Tee | Tank Nipple | Nipple-2in | Nipple-3in | Nipple-4in | Nipple-6in | Nipple-9in | Nipple-12in | Nipple-18in | GI/GI Flange | GI/HDP | HDPE/HDPE Flange set with adaptor | Globe Valve | Float Valve | CI Air Valve | Brass Union with Adapter | Saddle Ferrule | Flow Regulating | CI Sluice | Brass Ferule cock | Ball Valve
| 15 | m/no. | 203 | 80 | 962 | 893 | 52 | 169 | 47 | 30 | 56 |  |  |  | 139 | 131 |  | 25 | 37 | 50 | 76 | 113 | 151 | 227 | 964 |  |  | 924 | 1134 | 3756 | 245 |  | 1272 |  | 1505 | 514
| 20 | m/no. | 257 | 127 | 1198 | 1200 | 94 | 238 | 73 | 40 | 86 | 139 | 103 | 80 | 214 | 186 | 214 | 37 | 56 | 74 | 113 | 167 | 221 | 280 | 1183 |  |  | 1505 | 1283 | 5182 | 377 |  |  |  | 1961 | 650
| 25 | m/no. | 383 | 185 | 1930 | 1775 | 145 | 349 | 100 | 49 | 139 | 204 | 160 | 108 | 328 | 293 | 319 | 50 | 76 | 101 | 151 | 202 | 251 | 378 | 1453 |  |  | 1859 | 1556 | 5746 | 570 |  |  |  | 2879 | 872
| 32 | m/no. | 490 | 296 | 2756 | 2623 | 220 | 480 | 154 | 98 | 217 | 325 | 244 | 168 | 630 | 509 | 480 | 68 | 102 | 136 | 205 | 307 | 410 | 614 | 1699 | 1038 | 1038 | 2956 | 2690 |  | 742 |  |  |  |  | 1051
| 40 | m/no. | 565 | 410 | 3467 | 3035 | 308 | 594 | 208 | 124 | 275 | 451 | 342 | 226 | 952 | 611 | 611 | 83 |  | 166 | 253 | 413 | 505 | 755 | 1892 | 1322 | 1322 | 3713 | 4042 |  | 1322 | 354 |  | 6846 |  | 2035
| 50 | m/no. | 823 | 671 | 5519 | 5033 | 464 | 884 | 306 | 149 | 409 | 737 | 511 | 337 | 1393 | 990 | 990 | 127 | 188 | 256 | 379 | 569 | 757 | 1136 | 2348 | 1562 | 1562 | 4640 | 5381 |  | 1961 | 469 |  | 9132 |  | 3341
| 65 | m/no. | 1032 | 1054 | 11411 | 10225 | 805 | 1808 | 554 | 214 | 750 | 1160 | 883 | 602 | 3576 | 1670 | 1906 |  | 259 | 347 | 518 | 768 | 1022 | 1536 | 3358 | 1824 | 1824 | 9114 |  |  |  | 1306 |  | 11406
| 80 | m/no. | 1215 | 1424 | 14188 | 13657 | 1253 | 2436 | 817 | 437 | 938 | 1568 | 1361 | 860 | 5544 | 2420 | 2538 |  | 378 | 505 | 742 | 1136 | 1514 | 2249 | 3488 | 1950 | 1950 | 15060 |  |  |  | 1727 |  | 13691
| 100 | m/no. | 1883 | 2587 | 23238 | 19301 | 2159 | 3210 | 1415 | 838 | 1484 | 2866 | 2410 | 1552 | 7855 | 3268 | 3367 |  |  | 649 | 917 | 4871 | 1808 | 2743 | 6948 | 2406 | 2406 | 24350 |  |  |  | 2462 |  | 18250
| 125 | m/no. | 2440 | 7160 |  |  | 5342 | 7160 | 3534 |  |  | 7884 | 5878 | 4436 | [11 empty] | 3358 | 3814 | [6 empty] | 27737
| 150 | m/no. | 2767 | 8259 |  |  | 6430 | 8663 | 4752 |  |  | 9126 | 7073 | 5216 | [11 empty] | 3505 | 3505 | [6 empty] | 33288
| 200 | m/no. | 4243 | [22 empty] | 7627 | 7627 | [6 empty] | 46603
District Rate Available
| Diameter of pipe (mm) | Size in inch | Unit | PN6 | PN10 | PN12.5 | PN16 | Equal Tee (PN10)
| 20 | 0.5" | m | - | - |  | 37.13
| 25 | 0.75" | m | - | - | 47.58 | 57.2
| 32 | 1" | m | - | 64.35 | 75.35 | 92.95
| 40 | 1.25" | m | - | 99 | 119.35 | 143.83
| 50 | 1.5" | m | 100.38 | 152.63 | 185.08 | 222.2 | 110
| 63 | 2" | m | 156.2 | 242.55 | 287.93 | 349.25 | 210
| 75 | 2.5" | m | 224.4 | 343.2 | 407.28 | 495 | 320
| 90 | 3" | m | 315.7 | 491.43 | 589.6 | 712.53 | 540
| 110 | 4" | m | 464.2 | 726.83 | 873.68 | 1056 | 695
| 125 | 4.5" | m | 601.43 | 936.38 | 1124.48 | 1364.55 | 875
| 140 | 5" | m | 756.25 | 1171.78 | 1411.3 | 1707.48 | 1220
| 160 | 6" | m | 984.23 | 1528.73 | 1841.13 | 2236.85 | 1595
| 180 | 7" | m | 1242.45 | 1939.85 | 2328.15 | 2820.4 | 2335
| 200 | 8" | m | 1530.1 | 2391.95 | 2871.28 | 3483.43 | 2995
| 225 | 9" | m | 1942.88 | 3018.13 | 3634.68 | 4403.85 | 4190
| 250 | 10" | m | 2386.45 | 3718 | 4472.33 | 5433.45 | 5285
| 280 | 11" | m | 2993.38 | 4657.4 | 5608.08 | 6812.58 | 7395
| 315 | 12" | m | 3789.78 | 5901.23 | 7099.95 | 8609.43 | 9885
| 355 | 14" | m | 4803.43 | 7503.93 | 9012.85 | 10922.45
| 400 | 16" | m | 6210.33 | 9719.88 | 11683.93 | -
| 450 | 18" | m | 7856.48 | 12261.43 | 14779.05 | -
| 500 | 20" | m | 9713.28 | 15148.1 | 18219.03 | -
PipeCost (GI Medium Duty)
| Diameter of pipe | Unit | Pipe(Pg 64) | Tee (Pg 65) | Gate Valve | Check Valve | Elbow | Union | Socket | CI Plug | Hex Nipple | Re. Tee | Re. Elbow | Re Socket | Short bend | Cross Tee | Tank Nipple | Nipple-2in | Nipple-3in | Nipple-4in | Nipple-6in | Nipple-9in | Nipple-12in | Nipple-18in | GI/GI Flange | GI/HDP | HDPE/HDPE Flange set with adaptor | Globe Valve | Float Valve | CI Air Valve | Brass Union with Adapter | Saddle Ferrule | Flow Regulating | CI Sluice | Brass Ferule cock | Ball Valve
| 15 | m/no. | 172 | 80 | 962 | 893 | 52 | 169 | 47 | 30 | 56 |  |  |  | 139 | 131 |  | 25 | 37 | 50 | 76 | 113 | 151 | 227 | 964 |  |  | 924 | 1134 | 3756 | 245 |  | 1272 |  | 1505 | 514
| 20 | m/no. | 220 | 127 | 1198 | 1200 | 94 | 238 | 73 | 40 | 86 | 139 | 103 | 80 | 214 | 186 | 214 | 37 | 56 | 74 | 113 | 167 | 221 | 280 | 1183 |  |  | 1505 | 1283 | 5182 | 377 |  |  |  | 1961 | 650
| 25 | m/no. | 328 | 185 | 1930 | 1775 | 145 | 349 | 100 | 49 | 139 | 204 | 160 | 108 | 328 | 293 | 319 | 50 | 76 | 101 | 151 | 202 | 251 | 378 | 1453 |  |  | 1859 | 1556 | 5746 | 570 |  |  |  | 2879 | 872
| 32 | m/no. | 427 | 296 | 2756 | 2623 | 220 | 480 | 154 | 98 | 217 | 325 | 244 | 168 | 630 | 509 | 480 | 68 | 102 | 136 | 205 | 307 | 410 | 614 | 1699 | 1038 | 1038 | 2956 | 2690 |  | 742 |  |  |  |  | 1051
| 40 | m/no. | 490 | 410 | 3467 | 3035 | 308 | 594 | 208 | 124 | 275 | 451 | 342 | 226 | 952 | 611 | 611 | 83 | 126 | 166 | 253 | 413 | 505 | 755 | 1892 | 1322 | 1322 | 3713 | 4042 |  | 1322 | 354 |  | 6846 |  | 2035
| 50 | m/no. | 670 | 671 | 5519 | 5033 | 464 | 884 | 306 | 149 | 409 | 737 | 511 | 337 | 1393 | 990 | 990 | 127 | 188 | 256 | 379 | 569 | 757 | 1136 | 2348 | 1562 | 1562 | 4640 | 5381 |  | 1961 | 469 |  | 9132 |  | 3341
| 65 | m/no. | 855 | 1054 | 11411 | 10225 | 805 | 1808 | 554 | 214 | 750 | 1160 | 883 | 602 | 3576 | 1670 | 1906 |  | 259 | 347 | 518 | 768 | 1022 | 1536 | 3358 | 1824 | 1824 | 9114 |  |  |  | 1306 |  | 11406
| 80 | m/no. | 1060 | 1424 | 14188 | 13657 | 1253 | 2436 | 817 | 437 | 938 | 1568 | 1361 | 860 | 5544 | 2420 | 2538 |  | 378 | 505 | 742 | 1136 | 1514 | 2249 | 3488 | 1950 | 1950 | 15060 |  |  |  | 1727 |  | 13691
| 100 | m/no. | 1573 | 2587 | 23238 | 19301 | 2159 | 3210 | 1415 | 838 | 1484 | 2866 | 2410 | 1552 | 7855 | 3268 | 3367 |  |  | 649 | 917 | 4871 | 1808 | 2743 | 6948 | 2406 | 2406 | 24350 |  |  |  | 2462 |  | 18250
| 125 | m/no. | 2180 | 7160 |  |  | 5342 | 7160 | 3534 |  |  | 7884 | 5878 | 4436 | [11 empty] | 3358 | 3814 | [6 empty] | 27737
| 150 | m/no. | 2633 | 8259 |  |  | 6430 | 8663 | 4752 |  |  | 9126 | 7073 | 5216 | [11 empty] | 3505 | 3505 | [6 empty] | 33288
| 200 | m/no. | 4003 | [22 empty] | 7627 | 7627 | [6 empty] | 46603
For Truck analysis only
For Truck analysis only

## Analysis
Analysis of Labour & Material
[5 empty] | Labour (A) |  |  |  | Materials (B)
|  |  | Analyzed |  |  | Man | Rate | Amount | Type of |  |  | Unit | Total | Sub-Total | Contract. | Total | Unit
Sr. | Norms | Desciption of works | for |  | Category | Days | Rs. | Rs. | Materials | Quantity | Unit | Rate | Amount | (A+B) | O / head | Amount | Rate, Rs
No. | No. | [7 empty] | used |  |  | Rs. | Rs. |  |  | with 0/H
[6 empty] | 1 | 2 | 3 |  | 4 |  | 5 | 6 | 7 | 8 | 9 | 10
[8 empty] | 1x2 |  |  |  |  | 4x5 | 3+6 | 0.15x7 | 7+8
| 1 | Surface clearance
Felling of trees of dia 12-30 cm
1 | (1-1) | cutting of branches and lead |  |  | Labour | 0.13 | 920 | 119.6
|  | up to 15 m | 1 | No. |  |  | Total | 119.6 |  |  |  | Total | 0 | 119.6 | 17.94 | 137.54 | 137.54
Top Soil Excavation : Excavating
2 | (1-8) | 15-20 cm of the top soil including |  |  | Labour | 0.16 | 920 | 147.2
|  | disposal outside of the constr. site | 1 | Sq.m. |  |  | Total | 147.2 |  |  |  | Total | 0 | 147.2 | 22.08 | 169.28 | 169.28
3 |  | Site clearance |  |  | Unskilled | 0.17 | 920 | 156.4
|  |  | 1 | Sqm |  |  | Total | 156.4 |  |  |  | Total | 0 | 156.4 | 23.46 | 179.86 | 179.86
Trimming projections, filling
4 | (1-7) | depressions to level the surface etc. |  |  | Labour | 0.01 | 920 | 9.2
|  | (including service roads etc.) for 1 m2 | 1 | Sq.m. |  |  | Total | 9.2 |  |  |  | Total | 0 | 9.2 | 1.38 | 10.58 | 10.58
| 2 | Excavation Work
5 | (2-9) | Earthwork in Excavation in Soft Soil | 1 | Cum | Labour | 1 | 920 | 920 | T & P @3% of Labour Cost |  |  |  | 27.6 | 947.6 | 142.14 | 1089.74 | 1089.74
6 | 2 (12) | Earthwork in Excavation in Hard Soil | 1 | Cum | Labour | 1.25 | 920 | 1150 | T & P @3% of Labour Cost |  |  |  | 34.5 | 1184.5 | 177.675 | 1362.175 | 1362.18
7 | 2 (14) | Earthwork in Excavation in BMS | 1 | Cum | Labour | 1.59 | 920 | 1462.8 | T & P @3% of Labour Cost |  |  |  | 43.884 | 1506.684 | 226.0026 | 1732.6866 | 1732.69
8 | (2-15Ka) | Soft rock cutting in foundation, Drain | 1 | Cum | Labour | 3 | 920 | 2760 | T & P @3% of Labour Cost |  |  |  | 82.8 | 2842.8 | 426.42 | 3269.22 | 3269.22
9 | 2 (16-Kha) | Hard rock cutting | 1 | Cum | Labour | 25.2 | 920 | 23184 | T & P @3% of Labour Cost |  |  |  | 695.52 | 23879.52 | 3581.928 | 27461.448 | 27461.45
| 3 | Back Filling
10 | (2-39Ka) | with soft Soil | 1 | Cum | Labour | 0.5 | 920 | 460 | T & P @3% of Labour Cost |  |  |  | 13.8 | 473.8 | 71.07 | 544.87 | 544.87
11 | 2 (39-Ga) | Backfilling with Hard Soil | 1 | Cum | Labour | 0.63 | 920 | 579.6 | T & P @3% of Labour Cost |  |  |  | 17.388 | 596.988 | 89.5482 | 686.5362 | 686.54
12 | 2 (39-Gha) | Earthwork in Backfilling with BMS | 1 | Cum | Labour | 0.6 | 920 | 552 | T & P @3% of Labour Cost |  |  |  | 16.56 | 568.56 | 85.284 | 653.844 | 653.84
13 | 2 (39-Na) | Backfilling with Soft Rock | 1 | Cum | Labour | 1.1 | 920 | 1012 | T & P @3% of Labour Cost |  |  |  | 30.36 | 1042.36 | 156.354 | 1198.714 | 1198.71
| 4 | Stone Works | [12 empty] | 0
14 | 6-2 (2) | R.R. Masonry in mud mortar |  |  | Mason | 1 | 1225 | 1225 | Block Stone | 1.1 | Cum | 2575.99 | 2833.589 |  | 0
[5 empty] | Labour | 2.25 | 920 | 2070 | Mud | 0.42 | Cum | 343 | 144.06 |  | 0
|  |  | 1 | Cum |  |  | Total | 3295 |  |  |  | Total | 2977.649 | 6272.649 | 940.8973 | 7213.5463 | 7213.55
15 | 6-2 (1) | Dry stone masonry work |  |  | Mason | 1 | 1225 | 1225 | [6 empty] | 0
[5 empty] | Labour | 2 | 920 | 1840 | Block Stone | 1.1 | Cum | 2575.99 | 2833.589 |  | 0
|  |  | 1 | Cum |  |  | Total | 3065 |  |  |  | Total | 2833.589 | 5898.589 | 884.7883 | 6783.3773 | 6783.38
16 | 6 (5) | Dry boulder packing work | 1 | Cum | Labour | 1.5 | 920 | 1380 | Block Stone | 1.2 | Cum | 2575.99 | 3091.188 | 4471.188 | 670.6782 | 5141.8662 | 5141.87
17 | 11-16 | Boulder soling with sand |  |  | Mason | 1 | 1225 | 1225 | Block Stone | 1.1 | Cum | 2575.99 | 2833.589 |  | 0
[5 empty] | Labour | 3.5 | 920 | 3220 | Sand | 0.71 | Cum | 3175.88 | 2254.8748 |  | 0
|  |  | 1 | Cum |  |  | Total | 4445 |  |  |  | Total | 5088.4638 | 9533.4638 | 1430.0196 | 10963.4834 | 10963.48
18 | 6-1 (2) | R.R. masonry in 1:4 cement |  |  | Mason | 1.5 | 1225 | 1837.5 | Block Stone | 1.1 | Cum | 2575.99 | 2833.589 |  | 0
|  | mortar |  |  | Labour | 5 | 920 | 4600 | Cement | 3.18 | Bag | 700 | 2226 |  | 0
[9 empty] | Sand | 0.45 | Cum | 3175.88 | 1429.146 |  | 0
|  |  | 1 | Cum |  |  | Total | 6437.5 |  |  |  | Total | 6488.735 | 12926.235 | 1938.9352 | 14865.1703 | 14865.17
19 | 6-1 (3) | R.R. masonry in 1:6 cement |  |  | Mason | 1.5 | 1225 | 1837.5 | Block Stone | 1.1 | Cum | 2575.99 | 2833.589 |  | 0
|  | mortar |  |  | Labour | 5 | 920 | 4600 | Cement | 2.12 | Bag | 700 | 1484 |  | 0
[9 empty] | Sand | 0.47 | Cum | 3175.88 | 1492.6636 |  | 0
|  |  | 1 | Cum |  |  | Total | 6437.5 |  |  |  | Total | 5810.2526 | 12247.7526 | 1837.1629 | 14084.9155 | 14084.92
20 |  | R.R. masonry in 1:3 cement |  |  | Mason | 1.5 | 1225 | 1837.5 | Block Stone | 1.1 | Cum | 2575.99 | 2833.589 |  | 0
| 6-1(1) | mortar |  |  | Labour | 5 | 920 | 4600 | Cement | 3.88 | Bag | 700 | 2716 |  | 0
[9 empty] | Sand | 0.42 | Cum | 3175.88 | 1333.8696 |  | 0
|  |  | 1 | Cum |  |  | Total | 6437.5 |  |  |  | Total | 6883.4586 | 13320.9586 | 1998.1438 | 15319.1024 | 15319.1
21 |  | Gravel packing |  |  | Skilled | 1 | 1225 | 1225 | Aggregate | [5 empty] | 0
|  | 20,25 mm dia |  |  | Unskilled | 3.5 | 920 | 3220 | - 40 mm | 1.1 | Cum | 3352.32 | 3687.552 |  | 0
|  |  | 1 | Cum |  |  | Total | 4445 |  |  |  | Total | 3687.552 | 8132.552 | 1219.8828 | 9352.4348 | 9352.43
| 5 | Cement Concret Works
22 | 7-2 | Plain cement concrete (1:1:5:3) |  |  | Mason | 1 | 1225 | 1225 | Cement | 8 | Bag | 700 | 5600
[5 empty] | Labour | 4 | 920 | 3680 | Sand | 0.425 | Cum | 3175.88 | 1349.749
Aggregate
[9 empty] | - 10mm | 0.29 | Cum | 3352.32 | 972.1728
[9 empty] | - 20mm | 0.57 | Cum | 3352.32 | 1910.8224
|  |  | 1 | Cum |  |  | Total | 4905 |  |  |  | Total | 9832.7442 | 14737.7442 | 2210.6616 | 16948.4058 | 16948.41
23 | 7-2 Gha | Plain cement concrete (1:2:4) |  |  | Mason | 1 | 1225 | 1225 | Cement | 6.4 | Bag | 700 | 4480
[5 empty] | Labour | 4 | 920 | 3680 | Sand | 0.445 | Cum | 3175.88 | 1413.2666
Aggregate
[9 empty] | - 10mm | 0.11 | Cum | 3352.32 | 368.7552
[9 empty] | - 20mm | 0.22 | Cum | 3352.32 | 737.5104
[9 empty] | - 40mm | 0.52 | Cum | 3352.32 | 1743.2064
|  |  | 1 | Cum |  |  | Total | 4905 |  |  |  | Total | 8742.7386 | 13647.7386 | 2047.1608 | 15694.8994 | 15694.9
24 | 7-2 ga | Plain cement concrete (1:3:6) |  |  | Mason | 1 | 1225 | 1225 | Cement | 4.4 | Bag | 700 | 3080
[5 empty] | Labour | 4 | 920 | 3680 | Sand | 0.47 | Cum | 3175.88 | 1492.6636
Aggregate
[9 empty] | - 20mm | 0.24 | Cum | 3352.32 | 804.5568
[9 empty] | - 40mm | 0.65 | Cum | 3352.32 | 2179.008
|  |  | 1 | Cum |  |  | Total | 4905 |  |  |  | Total | 7556.2284 | 12461.2284 | 1869.1843 | 14330.4127 | 14330.41
25 | 7-5 | Mild steel reinforcement |  |  | Skilled | 0.12 | 1225 | 147 | MS Bars | 105 | Kg | 99 | 10395 |  | 0
[5 empty] | Unskilled | 0.12 | 920 | 110.4 | Bind Wire 12 | 1 | Kg | 92 | 92 |  | 0
|  |  | 100 | kg |  |  | Total | 257.4 |  |  |  | Total | 10487 | 10744.4 | 1611.66 | 12356.06 | 123.56
26 |  | Reinforcement including |  |  | Skilled | 0.25 | 1225 | 306.25 | MS bars | 2.59 | Kg | 99 | 256.41
|  | chicken wire, MS rods, GI wires |  |  | Unskilled | 0.08 | 920 | 73.6 | Bind Wire | 0.11 | Kg | 120 | 13.2
|  | etc for Ferro-cement works | [6 empty] | Chicken wire | 1.81 | M | 86 | 155.66
[9 empty] | GI plain wire | 2.08 | Kg | 124 | 257.92
|  |  | 1 | Sqm |  |  | Total | 379.85 |  |  |  | Total | 683.19 | 1063.04 | 159.456 | 1222.496 | 1222.5
| 6 | Form works | [12 empty] | 0
27 | 8-2-ka | Form work for concrete work |  |  | Skilled | 1.72 | 1225 | 2107 | Local wood | 0.11 | Cum | 57400 | 6314 |  | 0
[5 empty] | Unskilled | 2.57 | 920 | 2364.4 | Nails | 2.5 | Kg | 132 | 330 |  | 0
|  |  | 10 | Sqm |  |  | Total | 4471.4 |  |  |  | Total | 6644 | 11115.4 | 1667.31 | 12782.71 | 1278.27
27 | 8-2-ka | Form work for concrete work in arch,dome,etc ( Assuming form work canbe used 4 times) |  |  | Skilled | 1.72 | 1225 | 2107 | Local wood | 0.11 | Cum | 57400 | 6314 |  | 0
[5 empty] | Unskilled | 2.57 | 920 | 2364.4 | Nails | 2.5 | Kg | 132 | 330 |  | 0
|  |  | 10 | Sqm |  |  | Total | 4471.4 |  |  |  | Total | 6644 | 11115.4 | 1667.31 | 12782.71 | 1278.27
28 |  | HDPE pipe formwork for |  |  | Skilled | 0.17 | 1225 | 208.25 | Bind Wire | 0.08 | Kg | 120 | 9.6 |  | 0
|  | ferro-cement works |  |  | Unskilled | 0.11 | 920 | 101.2 | Bamboo | 0.33 | No. | 240 | 79.2 |  | 0
[9 empty] | Nails | 0.01 | Kg | 132 | 1.32 |  | 0
|  |  | 1 | Sqm |  |  | Total | 309.45 |  |  |  | Total | 90.12 | 399.57 | 59.9355 | 459.5055 | 459.51
| 7 | Roofing | [12 empty] | 0
29 | 9-1 | CGI sheet roofing |  |  | Skilled | 0.11 | 1225 | 134.75 | CGI sheet | 1.2 | Sqm | 470.6286 | 564.7543 |  | 0
[5 empty] | Unskilled | 0.13 | 920 | 119.6 | Nut and bolt | 3 | No. | 12.18 | 36.54 |  | 0
[9 empty] | J-hook | 2.5 | No. | 17.125 | 42.8125 |  | 0
[9 empty] | Bitumen- | [5 empty] | 0
[9 empty] | Washer | 5.5 | No. | 3 | 16.5 |  | 0
|  |  | 1 | Sqm |  |  | Total | 254.35 |  |  |  | Total | 660.6068 | 914.9568 | 137.2435 | 1052.2003 | 1052.2
30 | 9-2 | G.I plain sheet ridge work, |  |  | Carpenter | 0.2 | 1225 | 245 | G. I. Sheet | 1.2 | m. | 244.96 | 293.952 |  | 0
|  | collecting material all |  |  | Helper | 0.3 | 920 | 276 | Nut bolt | 4 | No. | 6.09 | 24.36 |  | 0
|  | complete for 1 rm. | 1 | R.m. |  |  | Total | 521 |  |  |  | Total | 318.312 | 839.312 | 125.8968 | 965.2088 | 965.21
| 8 | Wood works | [12 empty] | 0
31 | (10-1) | Salwood work for frames |  |  | Carpenter | 1.5 | 1225 | 1837.5 | Hard Wood | 0.044 | m3 | 214901.1917 | 9455.6524 |  | 0
|  | including fixing |  |  | Labourer | 0.15 | 920 | 138 | Holdfast 250 mm | 4 | No. | 21.14 | 84.56 |  | 0
|  | Size of door : 900 x 2100 mm | [6 empty] | Screws | 8 | No. | 3.3 | 26.4 |  | 0
|  | Size of wood : 100 x 75 mm | 1 | No. |  |  | Total | 1975.5 |  |  |  | Total | 9566.6124 | 11542.1124 | 1731.3169 | 13273.4293 | 13273.43
[5 empty] | Carpenter | 34 | 1225 | 41650 | Hard Wood | 1.1 | m3 | 214901.1917 | 236391.3108 |  | 0
[5 empty] | Labourer | 3.4 | 920 | 3128 | Hold fast | 92 | No. | 21.14 | 1944.88 |  | 0
[9 empty] | Screws | 184 | No. | 3.3 | 607.2 |  | 0
|  |  | 1 | m3 |  |  | Total | 44778 |  |  |  | Total | 238943.3908 | 283721.3908 | 42558.2086 | 326279.5995 | 326279.6
32 | (10-2) | 38 mm thick Salwood frame for |  |  | Carpenter | 10 | 1225 | 12250 | Hard Wood | 0.084 | m3 | 214901.1917 | 18051.7001 |  | 0
|  | panelled door shutter for 1 No. |  |  | Labourer | 1 | 920 | 920 | Hinge 150 mm | 6 | No. | 59 | 354 |  | 0
|  | Shutter size : 1.07 x 1.982 | [6 empty] | Tower bolt | [5 empty] | 0
|  | = for 2.12074 m2 | [6 empty] | 150 mm | 1 | No. | 71 | 71 |  | 0
[9 empty] | Tower bolt | [5 empty] | 0
[9 empty] | 300 mm | 1 | No. | 114 | 114 |  | 0
[9 empty] | Locking set | [5 empty] | 0
[9 empty] | 250 mm | 1 | No. | 277 | 277 |  | 0
[9 empty] | Handle | 2 | No. | 159 | 318 |  | 0
[9 empty] | Screw & nail | 1 | L.S. | 165 | 165 |  | 0
|  |  | 2.1207 | m2 |  |  | Total | 13170 |  |  |  | Total | 19350.7001 | 32520.7001 | 4878.105 | 37398.8051 | 17634.79
33 | (10-10) | 38 mm thick Salwood |  |  | Carpenter | 5 | 1225 | 6125 | Hard Wood | 0.026 | m3 | 214901.1917 | 5587.431 |  | 0
|  | SWG G.I. wire mesh for mosquito |  |  | Labourer | 0.5 | 920 | 460 | Wire mesh | [5 empty] | 0
|  | proof shutter for 1 No. | [6 empty] | 24 SWG | 2.13 | m2 | 100 | 213 |  | 0
|  | Shutter size : 1.092 x 2.05 | [6 empty] | Hinge 100 mm | 3 | No. | 59 | 177 |  | 0
[9 empty] | Tower bolt | [5 empty] | 0
[9 empty] | 150 mm | 2 | No. | 71 | 142 |  | 0
[9 empty] | Handle | 2 | No. | 159 | 318 |  | 0
[9 empty] | Spring | 1 | No. | 190 | 190 |  | 0
[9 empty] | Screw & nail |  | L.S. | 165 | 165 |  | 0
|  |  | 2.24 | m2 |  |  | Total | 6585 |  |  |  | Total | 6792.431 | 13377.431 | 2006.6146 | 15384.0456 | 6867.88
34 |  | 38 mm thick wooden |  |  | Carpenter | 3.12 | 1225 | 3822 | Sal Wood | 0.02 | Cum | 214901.1917 | 4298.0238 |  | 0
|  | shutter with 24 SWG |  |  | Helper | 0.31 | 920 | 285.2 | Nails | L.S. | Kg | 132 | 132 |  | 0
|  | plain sheet on one side | [6 empty] | Hinges100 mm | 1.34 | No. | 59 | 79.06 |  | 0
[9 empty] | Locking set | 0.45 | No. | 277 | 124.65 |  | 0
[9 empty] | Tower bolt150 | 0.89 | No. | 71 | 63.19 |  | 0
[9 empty] | Handle | 0.45 | No. | 159 | 71.55 |  | 0
[9 empty] | Hold fast | 1.78 | No. | 21.14 | 37.6292 |  | 0
[9 empty] | GI plain sheet | 2.07 | Sqm | 462.7057 | 957.8008 |  | 0
|  |  | 1 | Sqm |  |  | Total | 4107.2 |  |  |  | Total | 5763.9039 | 9871.1039 | 1480.6656 | 11351.7694 | 11351.77
35 | 10-17 | Wood works for beam, |  |  | Skilled | 17.65 | 1225 | 21621.25 | Local wood | 1.05 | Cum | 57400 | 60270 |  | 0
|  | rafters etc. |  |  | Unskilled | 1.76 | 920 | 1619.2 | [6 empty] | 0
|  |  | 1 | Cum |  |  | Total | 23240.45 |  |  |  | Total | 60270 | 83510.45 | 12526.5675 | 96037.0175 | 96037.02
| 10 | Plastering Works | [12 empty] | 0
36 | 12-1- | 12.5mm thick cement |  |  | Skilled | 12 | 1225 | 14700 | Cement | 18 | Bag | 700 | 12600 |  | 0
| ka | plaster (1:2) |  |  | Unskilled | 16 | 920 | 14720 | Sand | 1.22 | Cum | 3175.88 | 3874.5736 |  | 0
|  |  | 100 | Sqm |  |  | Total | 29420 |  |  |  | Total | 16474.5736 | 45894.5736 | 6884.186 | 52778.7596 | 527.79
37 | 12-1- | 12.5mm thick cement ) |  |  | Skilled | 12 | 1225 | 14700 | Cement | 12.5 | Bag | 700 | 8750 |  | 0
| kha | plaster (1:3 |  |  | Unskilled | 16 | 920 | 14720 | Sand | 1.28 | Cum | 3175.88 | 4065.1264 |  | 0
|  |  | 100 | Sqm |  |  | Total | 29420 |  |  |  | Total | 12815.1264 | 42235.1264 | 6335.269 | 48570.3954 | 485.7
38 | 12-1-ga | 12.5mm thick cement |  |  | Skilled | 12 | 1225 | 14700 | Cement | 10.76 | Bag | 700 | 7532 |  | 0
|  | plaster (1:4) |  |  | Unskilled | 16 | 920 | 14720 | Sand | 1.46 | Cum | 3175.88 | 4636.7848 |  | 0
|  |  | 100 | Sqm |  |  | Total | 29420 |  |  |  | Total | 12168.7848 | 41588.7848 | 6238.3177 | 47827.1025 | 478.27
39 | 12-4-ka | 20mm thick cement |  |  | Skilled | 14 | 1225 | 17150 | Cement | 19.2 | Bag | 700 | 13440 |  | 0
|  | plaster (1:3) |  |  | Unskilled | 19 | 920 | 17480 | Sand | 1.95 | Cum | 3175.88 | 6192.966 |  | 0
|  |  | 100 | Sqm |  |  | Total | 34630 |  |  |  | Total | 19632.966 | 54262.966 | 8139.4449 | 62402.4109 | 624.02
40 | 12-4- | 20mm thick cement |  |  | Skilled | 14 | 1225 | 17150 | Cement | 16.2 | Bag | 700 | 11340 |  | 0 |  |  | 810.6
| kha | plaster (1:4) |  |  | Unskilled | 19 | 920 | 17480 | Sand | 2.2 | Cum | 3175.88 | 6986.936 |  | 0
|  |  | 100 | Sqm |  |  | Total | 34630 |  |  |  | Total | 18326.936 | 52956.936 | 7943.5404 | 60900.4764 | 609
41 | 12-4-ga | 20mm thick cement |  |  | Skilled | 14 | 1225 | 17150 | Cement | 11.4 | Bag | 700 | 7980 |  | 0
|  | plaster (1:6) |  |  | Unskilled | 19 | 920 | 17480 | Sand | 2.35 | Cum | 3175.88 | 7463.318 |  | 0
|  |  | 100 | Sqm |  |  | Total | 34630 |  |  |  | Total | 15443.318 | 50073.318 | 7510.9977 | 57584.3157 | 575.84
42 | 14-2- | Flush ruled pointing work(1:3) |  |  | Skilled | 10 | 1225 | 12250 | Cement | 6.12 | Bag | 700 | 4284 |  | 0
| gha |  |  |  | Unskilled | 14 | 920 | 12880 | Sand | 0.63 | Cum | 3175.88 | 2000.8044 |  | 0
|  |  | 100 | Sqm |  |  | Total | 25130 |  |  |  | Total | 6284.8044 | 31414.8044 | 4712.2207 | 36127.0251 | 361.27
43 | 8-2-ka | 3 mm thick cement punning |  |  | Skilled | 10 | 1225 | 12250 | Cement | 10.64 | Bag | 700 | 7448 |  | 0
[5 empty] | Unskilled | 10 | 920 | 9200 | [6 empty] | 0
|  |  | 100 | Sqm |  |  | Total | 21450 |  |  |  | Total | 7448 | 28898 | 4334.7 | 33232.7 | 332.33
| 11 | Painting | [12 empty] | 0
44 | 13-12 | Two coats cement painting |  |  | Painter | 0.065 | 1225 | 79.625 | Cement Paint | 0.5 | kg | 69 | 34.5 |  | 0
| kha |  |  |  | Labour | 0.065 | 920 | 59.8 | (Snowecem) | [5 empty] | 0
|  |  | 1 | Sqm |  |  | Total | 139.425 |  |  |  | Total | 34.5 | 173.925 | 26.0888 | 200.0138 | 200.01
45 | 13-5 ka | Two coats of enamel painting |  |  | Painter | 0.12 | 1225 | 147 | Primer | 0.08 | Ltr | 288 | 23.04 |  | 0
| 13-5 kha | with one coat of primer |  |  | Unskilled | 0.08 | 920 | 73.6 | Enamel Paint | 0.16 | Ltr | 534 | 85.44 |  | 0
|  |  | 1 | Sqm |  |  | Total | 220.6 |  |  |  | Total | 108.48 | 329.08 | 49.362 | 378.442 | 378.44
46 | 13-1Ka | Two coats of bitumen painting |  |  | Painter | 0.03 | 1225 | 36.75 | Bitumen Paint | 0.12 | Ltr | 249.73 | 29.9676 |  | 0
[5 empty] | Unskilled | 0.02 | 920 | 18.4 | [6 empty] | 0
|  |  | 1 | Sqm |  |  | Total | 55.15 |  |  |  | Total | 29.9676 | 85.1176 | 12.7676 | 97.8852 | 97.89
47 |  | Laying of one layer of |  |  | Skilled | 0.06 | 1225 | 73.5 | Polythene- | 1 | Sqm | 33 | 33 |  | 0
|  | 500 gauge |  |  | Unskilled | 0.06 | 920 | 55.2 | Sheet | [5 empty] | 0
|  | of Polythene sheet | 1 | Sqm |  |  | Total | 128.7 |  |  |  | Total | 33 | 161.7 | 24.255 | 185.955 | 185.96
48 | 16.03 | Tarfelt laying for 1 m2 in : |  |  | Skilled | 0.11 | 1225 | 134.75 | Tarfelt | 1.1 | m2 | 140 | 154 |  | 0
| (18-12Ka) | One layer |  |  | Unskilled | 0.35 | 920 | 322 | Bitumen | 1.5 | Kg | 30 |  |  | 0
[9 empty] | Firewood | 6 | Kg | 3 |  |  | 0
[9 empty] | Coarse sand | 0.031 | m3 | 3175.88 |  |  | 0
|  |  | 1 | Sqm |  |  | Total | 456.75 |  |  |  | Total | 154 | 610.75 | 91.6125 | 702.3625 | 702.36
| 12 | Protection Work | [12 empty] | 0
49 | 16-2 ka | 28.1 Gabion preparation, |  |  | Skilled | 0.5 | 1225 | 612.5 | GI plain wire | 28.4 | Kg | 124 | 3521.6 |  | 0
|  | mesh forming etc. |  |  | Unskilled | 0.2 | 920 | 184 | Salvage wire | 3.15 | Kg | 92 | 289.8 |  | 0
|  | (2 m x1 m x 1 m) | 2 | Cum |  |  | Total | 796.5 |  |  |  | Total | 3811.4 | 4607.9 | 691.185 | 5299.085 | 2649.54
50 | 16-2 ka | 28.1 Gabion preparation, |  |  | Skilled | 0.7 | 1225 | 857.5 | GI plain wire | 41.3 | Kg | 124 | 5121.2 |  | 0
|  | mesh forming etc. |  |  | Unskilled | 0.28 | 920 | 257.6 | Salvage wire | 4.1 | Kg | 92 | 377.2 |  | 0
|  | (3 m x1 m x 1 m) | 3 | Cum |  |  | Total | 1115.1 |  |  |  | Total | 5498.4 | 6613.5 | 992.025 | 7605.525 | 2535.18
51 | 16-11 | 28.2 Filling of Gabion box | 1 | Cum | Unskilled | 0.5 | 920 | 460 | Stone | 1.1 | Cum | 2575.99 | 2833.589 | 3293.589 | 494.0383 | 3787.6273 | 3787.63
|  | with stone | [12 empty] | 0
| 13 | Pipe laying and jointing | [12 empty] | 0
52 | 17-2 | HDPE pipe jointing works |  |  | Plumber | 1 | 1225 | 1225 | T & P @3% of Labour Cost |  |  |  | 119.55 |  | 0
|  | 20,25 mm dia |  |  | Helper | 1 | 920 | 920 | Misc.Expences @2.5% |  |  |  | 99.625 |  | 0
[5 empty] | Labour | 2 | 920 | 1840 | Fuel | 0.25 | Lit | 147.79 | 36.9475 |  | 0
|  |  | 1000 | m |  |  | Total | 3985 |  |  |  | Total | 256.1225 | 4241.1225 | 636.1684 | 4877.2909 | 4.88
53 | 17-2 | HDPE pipe jointing works |  |  | Plumber | 1 | 1225 | 1225 | T & P @3% of Labour Cost |  |  |  | 147.15 |  | 0
|  | 32 mm dia |  |  | Helper | 1 | 920 | 920 | Misc.Expences @2.5% |  |  |  | 147.15 |  | 0
[5 empty] | Labour | 3 | 920 | 2760 | Fuel | 0.25 | Lit | 147.79 | 36.9475 |  | 0
|  |  | 1000 | m |  |  | Total | 4905 |  |  |  | Total | 331.2475 | 5236.2475 | 785.4371 | 6021.6846 | 6.02
54 | 17-2 | HDPE pipe jointing works |  |  | Plumber | 1.5 | 1225 | 1837.5 | T & P @3% of Labour Cost |  |  |  | 179.325 |  | 0
|  | 40,50 mm dia |  |  | Helper | 1.5 | 920 | 1380 | Misc.Expences @2.5% |  |  |  | 149.4375 |  | 0
[5 empty] | Labour | 3 | 920 | 2760 | Fuel | 0.37 | Lit | 147.79 | 54.6823 |  | 0
|  |  | 1000 | m |  |  | Total | 5977.5 |  |  |  | Total | 383.4448 | 6360.9448 | 954.1417 | 7315.0865 | 7.32
55 | 17-2 | HDPE pipe jointing works |  |  | Plumber | 1 | 1225 | 1225 | T & P @3% of Labour Cost |  |  |  | 119.55 |  | 0
|  | 63,90 mm dia |  |  | Helper | 1 | 920 | 920 | Misc.Expences @2.5% |  |  |  | 99.625 |  | 0
[5 empty] | Labour | 2 | 920 | 1840 | Fuel | 0.05 | Lit | 147.79 | 7.3895 |  | 0
|  |  | 50 | m |  |  | Total | 3985 |  |  |  | Total | 226.5645 | 4211.5645 | 631.7347 | 4843.2992 | 96.87
56 | 17-2 | HDPE pipe jointing works |  |  | Plumber | 1.5 | 1225 | 1837.5 | T & P @3% of Labour Cost |  |  |  | 119.55 |  | 0
|  | 110, 125 mm dia |  |  | Helper | 1.5 | 920 | 1380 | Misc.Expences @2.5% |  |  |  | 99.625 |  | 0
[5 empty] | Labour | 3 | 920 | 2760 | Fuel | 0.05 | Lit | 147.79 | 7.3895 |  | 0
|  |  | 50 | m |  |  | Total | 5977.5 |  |  |  | Total | 226.5645 | 6204.0645 | 930.6097 | 7134.6742 | 142.69
57 | 17-2 | HDPE pipe jointing works |  |  | Plumber | 2 | 1225 | 2450 | T & P @3% of Labour Cost |  |  |  | 119.55 |  | 0
|  | 140, 160 & 180 mm dia |  |  | Helper | 2 | 920 | 1840 | Misc.Expences @2.5% |  |  |  | 99.625 |  | 0
[5 empty] | Labour | 4 | 920 | 3680 | Fuel | 0.05 | Lit | 147.79 | 7.3895 |  | 0
|  |  | 50 | m |  |  | Total | 7970 |  |  |  | Total | 226.5645 | 8196.5645 | 1229.4847 | 9426.0492 | 188.52
58 | 17-4-ka | GI pipe jointing works |  |  | Plumber | 0.5 | 1225 | 612.5 | Lead, Hemp etc @10% |  |  |  | 245.25 |  | 0
|  | 15,20 mm dia |  |  | Helper | 1 | 920 | 920 | Misc.Expences @2.5% |  |  |  | 61.3125 |  | 0
[5 empty] | Labour | 1 | 920 | 920 | [6 empty] | 0
|  |  | 30 | m |  |  | Total | 2452.5 |  |  |  | Total | 306.5625 | 2759.0625 | 413.8594 | 3172.9219 | 105.76
59 | 17-4-ka | GI pipe jointing works |  |  | Plumber | 0.5 | 1225 | 612.5 | Lead, Hemp etc @10% |  |  |  | 337.25 |  | 0
|  | 25,32 mm dia |  |  | Helper | 1.5 | 920 | 1380 | Misc.Expences @2.5% |  |  |  | 84.3125 |  | 0
[5 empty] | Labour | 1.5 | 920 | 1380 | [6 empty] | 0
|  |  | 30 | m |  |  | Total | 3372.5 |  |  |  | Total | 421.5625 | 3794.0625 | 569.1094 | 4363.1719 | 145.44
60 | 17-4-ka | GI pipe jointing works |  |  | Plumber | 0.75 | 1225 | 918.75 | Lead, Hemp etc @10% |  |  |  | 459.875 |  | 0
|  | 40,50 mm dia |  |  | Helper | 2 | 920 | 1840 | Misc.Expences @2.5% |  |  |  | 114.9688 |  | 0
[5 empty] | Labour | 2 | 920 | 1840 | [6 empty] | 0
|  |  | 30 | m |  |  | Total | 4598.75 |  |  |  | Total | 574.8438 | 5173.5938 | 776.0391 | 5949.6328 | 198.32
61 | 17-4-ka | GI pipe jointing works |  |  | Plumber | 1.25 | 1225 | 1531.25 | Lead, Hemp etc @10% |  |  |  | 613.125 |  | 0
|  | 65,80 mm dia |  |  | Helper | 2 | 920 | 1840 | Misc.Expences @2.5% |  |  |  | 153.2812 |  | 0
[5 empty] | Labour | 3 | 920 | 2760 | [6 empty] | 0
|  |  | 30 | m |  |  | Total | 6131.25 |  |  |  | Total | 766.4062 | 6897.6562 | 1034.6484 | 7932.3047 | 264.41
62 | 17-4-ka | GI pipe jointing works |  |  | Plumber | 1.75 | 1225 | 2143.75 | Lead, Hemp etc @10% |  |  |  | 766.375 |  | 0
|  | 100 mm dia |  |  | Helper | 2 | 920 | 1840 | Misc.Expences @2.5% |  |  |  | 191.5938 |  | 0
[5 empty] | Labour | 4 | 920 | 3680 | [6 empty] | 0
|  |  | 30 | m |  |  | Total | 7663.75 |  |  |  | Total | 957.9688 | 8621.7188 | 1293.2578 | 9914.9766 | 330.5
63 | 17-4-ka | GI pipe jointing works |  |  | Plumber | 2 | 1225 | 2450 | Lead, Hemp etc @10% |  |  |  | 935 |  | 0
|  | 125 mm dia |  |  | Helper | 2.5 | 920 | 2300 | Misc.Expences @2.5% |  |  |  | 233.75 |  | 0
[5 empty] | Labour | 5 | 920 | 4600 | [6 empty] | 0
|  |  | 30 | m |  |  | Total | 9350 |  |  |  | Total | 1168.75 | 10518.75 | 1577.8125 | 12096.5625 | 403.22
63 | 17-4-ka | GI pipe jointing works |  |  | Plumber | 2 | 1225 | 2450 | Lead, Hemp etc @10% |  |  |  | 1073 |  | 0
|  | 150 mm dia |  |  | Helper | 3 | 920 | 2760 | Misc.Expences @2.5% |  |  |  | 268.25 |  | 0
[5 empty] | Labour | 6 | 920 | 5520 | [6 empty] | 0
|  |  | 30 | m |  |  | Total | 10730 |  |  |  | Total | 1341.25 | 12071.25 | 1810.6875 | 13881.9375 | 462.73
| 14 | Fencing Works | [12 empty] | 0
64 | 24-7 | Barbed wire fencing on w |  |  | Skilled | 1 | 1225 | 1225 | Local wood | 0.19 | Cum | 57400 | 10906 |  | 0
|  | ooden posts (2 diagonals |  |  | Unskilled | 2 | 920 | 1840 | Barbed wire | 250 | m | 10.08 | 2520 |  | 0
|  | & 5 horizontals) | [6 empty] | U hooks | 77 | No. | 17.125 | 1318.625 |  | 0
|  | @ 3 m c\c | 30 | Rm |  |  | Total | 3065 |  |  |  | Total | 14744.625 | 17809.625 | 2671.4437 | 20481.0687 | 682.7
65 | 24-6 | Barbed wire fencing |  |  | Skilled | 1.08 | 1225 | 1323 | Barbed wire | 110 | m | 10.08 | 1108.8 |  | 0
[5 empty] | Unskilled | 5.38 | 920 | 4949.6 | [6 empty] | 0
|  |  | 100 | Rm |  |  | Total | 6272.6 |  |  |  | Total | 1108.8 | 7381.4 | 1107.21 | 8488.61 | 84.89
66 | 24-7 | Barbed wire fencing on |  |  | Skilled | 2 | 1225 | 2450 | PCC ( 1:1.5:3 ) | 0.33 | Cum | 14737.7442 | 4863.4556 |  | 0
|  | RCC Posts |  |  | Unskilled | 5.31 | 920 | 4885.2 | MS Rod 8 & 6 | 36.46 | kg | 99 | 3609.54 |  | 0
|  | (100 mm X 100 X 2.2 m ) @ 2 m c/c | [6 empty] | Formworks | 13.2 | m2 | 1278.27 | 16873.164 |  | 0
|  | (2 diagonals & 5 horizontals) | [6 empty] | Binding wire | 0.36 | kg | 92 | 33.12 |  | 0
[9 empty] | Barbed wire | 250 | m | 10.08 | 2520 |  | 0
[9 empty] | U hooks | 116 | No. | 17.125 | 1986.5 |  | 0
|  |  | 30 | Rm |  |  | Total | 7335.2 |  |  |  | Total | 29885.7796 | 37220.9796 | 5583.1469 | 42804.1265 | 1426.8
67 | 5-1(kha 2) | Chimney made Brick work in |  |  | Mason | 1.5 | 1225 | 1837.5 | Brick | 560 | No. | 15.145 | 8481.2 |  | 0
|  | 1:4 cement mortar |  |  | Labour | 4.2 | 920 | 3864 | Cement | 2 | Bag | 700 | 1400 |  | 0
[9 empty] | Sand | 0.28 | Cum | 3175.88 | 889.2464 |  | 0
|  |  | 1 | Cum |  |  | Total | 5701.5 |  |  |  | Total | 10770.4464 | 16471.9464 | 2470.792 | 18942.7384 | 18942.74
68 | 5-1(kha 3) | Chimney made Brick work in |  |  | Mason | 1.5 | 1225 | 1837.5 | Brick | 560 | No. | 15.145 | 8481.2 |  | 0
|  | 1:6 cement mortar |  |  | Labour | 4.2 | 920 | 3864 | Cement | 1.4 | Bag | 700 | 980 |  | 0
[9 empty] | Sand | 0.3 | Cum | 3175.88 | 952.764 |  | 0
|  |  | 1 | Cum |  |  | Total | 5701.5 |  |  |  | Total | 10413.964 | 16115.464 | 2417.3196 | 18532.7836 | 18532.78
69 | 11-15(ka) | Flat brick soling |  |  | Mason | 0.05 | 1225 | 61.25 | Brick | 42 | No. | 15.145 | 636.09 |  | 0
[5 empty] | Labour | 0.1 | 920 | 92 | Sand | 0.07 | Cum | 3175.88 | 222.3116 |  | 0
0
|  |  | 1 | Sq.m |  |  | Total | 153.25 |  |  |  | Total | 858.4016 | 1011.6516 | 151.7477 | 1163.3993 | 1163.4

## Mat-Collect_2
ANALYSIS OF RATES
MATERIAL COLLECTION AND TRANSPORTATION
A. | Transportation
1 | Transportation of easy loads from ........... to Project site - For 1 kg
Manually
| Cost of transportation to project site | 0 |  |  |  | 0
| Contractor's overhead and value added tax @ | 29.95 | % |  |  | 0
| Rate of Transportation per kg |  |  |  | Rs. | 0
2 | Transportation of difficult load from ........... to Project site - For 1 kg
manually
| Cost of transportation to project site | 0 |  |  |  | 0
| Contractor's overhead and value added tax @ | 29.95 | % |  |  | 0
| Rate of Transportation per kg |  |  |  | Rs. | 0
3 | Transportation of easy loads from ........... to Project site - For 1 kg
| Total transportation cost for one kg | 0 |  |  |  | 0
| Contractor's overhead and value added tax @ | 29.95 | % |  |  | 0
| Rate of Transportation per kg |  |  |  | Rs. | 0
4 | Transportation of difficult loads from ........... to Project site - For 1 kg
| Total transportation cost for one kg | 0 |  |  |  | 0
| Contractor's overhead and value added tax @ | 29.95 | % |  |  | 0
| Rate of Transportation per kg |  |  |  | Rs. | 0
5 | Transportation of Pipes from ........... to Project site - For 1 kg
| Total transportation cost for difficult load for one kg | 0 |  |  | Total | 0
| Contractor's overhead and value added tax @ | 29.95 | % |  |  | 0
| Rate of Transportation per kg |  |  |  | Rs. | 0
B. | Construction Materials
1 | Cement - For 1 (per bag)
| Cost of one bag (50 kg.) of cement at ...........@ | 700 | Rs./bag |  |  | 700
| Transportation cost for one kg to project site | 0 | Rs. per Kg
Transportation of a bag of cement from ...........
| to treatment plant site |  |  |  |  | 0
Load/Unload
| Total Cost of cement / bag at construction site |  |  |  |  | 700
| Total Cost of cement / tonne at construction site |  |  |  |  | 14000
|  | Rate for 1 metric tonne = |  |  | Rs. | 14000
|  | Rate for 1 bag = |  |  | Rs. | 700
2 | Reinforcement Steel - For 1 Metric tonne.
| Cost of one ton of Reinforcement Bar at ........... @ | 99000 | Rs./MT |  |  | 99000
Transportation cost for one kg of Reinforcement
| of Steel to project site | 0 | Rs. per Kg
Transportation cost for one tonne of Reinforcement
| of Steel to project site |  |  |  |  | 0
Load/Unload for one tone
| Total Cost of Reinforcement Steel / tone at construction site |  |  |  |  | 99000
|  | Rate for 1 metric tonne = |  |  | Rs. | 99000
|  | Rate per kg = |  |  |  | 99
3 | Sand for 1 cu.m.
| Approved District Rate of sand | 3175.8797 | Rs./cum |  |  | 3175.8797
| Transportation cost of sand up to site per kg | 0 | Rs. per Kg
| Unit weight of sand | 1600 | kg/ cu.m
| Cost of Transportation/cum at construction site |  |  |  |  | 0
Load/Unload for one cu.m
| Total Cost of sand / cum at construction site |  |  |  |  | 3175.88
|  | Rate for 1 cu. m. = |  |  | Rs. | 3175.88
4 | Blockstone - For 1 cu. m.
| Approved District Rate of Block Stone | 2575.9913 | Rs./cum |  |  | 2575.9913
| Therefore rate per cum of blockstone = |  |  |  | = | 2575.9913
| Transportation cost of Block Stone | 0 | Rs. per Kg
| Unit weight of Block Stone | 2400 | kg/ cu.m
| Cost of Transportation/cum at construction site |  |  |  |  | 0
| Total Cost of Blockstone / cum at construction site |  |  |  |  | 2575.99
|  | Rate for 1 cu. m. = |  |  | Rs. | 2575.99
5 | Bondstone - For 1 cu. m.
| Approved District Rate of Bond Stone | 2575.9913 | Rs./cum |  |  | 2575.9913
| Therefore rate per cum of blockstone = |  |  |  | = | 2575.9913
| Transportation cost of Bond Stone | 0 | Rs. per Kg
| Unit weight of Bond Stone | 2400 | kg/ cu.m
| Cost of Transportation/cum at construction site |  |  |  |  | 0
| Total Cost of Bondstone / cum at construction site |  |  |  |  | 2575.99
|  | Rate for 1 cu. m. = |  |  | Rs. | 2575.99
6 | Aggregates (40 - 70 mm size ) - For 1 cu. m
| Approved District Rate of aggregate | 3352.3174 | Rs./cum |  |  | 3352.3174
| Therefore rate per cum of aggregate |  |  |  | = | 3352.3174
| Transportation cost of aggregate | 0 | Rs. per Kg
| Unit weight of aggregate | 2200 | kg/ cu.m
| Cost of Transportation/cum at construction site |  |  |  |  | 0
Load/Unload for one cu.m
| Total Cost of Aggregates / cum at construction site |  |  |  |  | 3352.32
|  | Rate for 1 cu. m. = |  |  | Rs. | 3352.32
7 | Aggregates (20 - 40 mm size ) - For 1 cu. m
| Approved District Rate of aggregate | 3352.3174 | Rs./cum |  |  | 3352.3174
| Therefore rate per cum of aggregate |  |  |  | = | 3352.3174
| Transportation cost of aggregate | 0 | Rs. per Kg
| Unit weight of aggregate | 2200 | kg/ cu.m
| Cost of Transportation/cum at construction site |  |  |  |  | 0
Load/Unload for one cu.m
| Total Cost of Aggregates / cum at construction site |  |  |  |  | 3352.32
|  | Rate for 1 cu. m. = |  |  | Rs. | 3352.32
8 | Aggregates (10 - 20 mm size ) - For 1 cu. m
| Approved District Rate of aggregate | 3352.3174 | Rs./cum |  |  | 3352.3174
| Therefore rate per cum of aggregate |  |  |  |  | 3352.3174
| Transportation cost of aggregate | 0 | Rs. per Kg
| Unit weight of aggregate | 2200 | kg/ cu.m
| Cost of Transportation/cum at construction site |  |  |  |  | 0
Load/Unload for one cu.m
| Total Cost of Aggregates / cum at construction site |  |  |  |  | 3352.32
|  | Rate for 1 cu. m. = |  |  | Rs. | 3352.32
9 | Filter Media (Sand)
Seiving of the sand through the wire mesh
of required size to get the specified filter sand
and then packing in jute bags
a) 3-1 kha | Collection, separation and lead up to 10 m for quarry capacity cum
| 31 -50 % | 3.45 | md | 920 |  | 3174
3-12 kha | Seiving of sand through two sized screens passing through D10 size and retaining on D60 | 10 | md | 920 |  | 9200
3-12 kha | Washing of sand cum | 2 | md | 920 |  | 1840
d) | Packing of sieved sand in jute bags L.S. | 0.5 | md | 920 |  | 460
e) | Cost of 45 jute bags for packing of 1 cum of sand @ Rs. 10.00 per piece | 45 |  | 5 |  | 225
f) | Loading Unloading charge | 45 |  | 6 |  | 270
Transportation of filter media
h) | Transportation of easy load by per kg | 0 | Rs. per Kg
| Weight of sand @ 1600 kg/cu.m | 1600 | kg
| Total for transportation of 1 cu. m. sand |  |  |  |  | 0
i) | Laying of the filter Sand Media (Labour cost only)
| Skilled labour 0.65 nos. | 0.65 |  | 1225 |  | 796.25
|  | Sub Total for 1 cu. m. = |  |  | Rs. | 15965.25
| Contractor's overhead and value added tax @ | 29.95 | % |  | Rs. | 4781.59
Total Rate per cu.m of filter Sand
| including material and labour with transportation |  |  |  | Rs. | 20746.84
10 | Filter Media (Gravel) [2 mm to 5 mm]
Collection, seiving of the gravel through the wire mesh of required size to get the specified filter gravel and stocking with lead up to 10 m and then packing in jute bags
a) 3-2 ga | Collection, separation and lead up to 10 m for quarry capacity cum
| 4-10 mm size | 10 | md | 920 |  | 9200
b) 3-2 kha | Washing of gravel cum | 1.75 | md | 920 |  | 1610
c) | Packing of sieved gravel in jute bags L.S. | 0.5 | md | 920 |  | 460
d) | Cost of 45 jute bags for packing of 1 cum of sand @ Rs. 10.00 per piece | 45 |  | 5 |  | 225
e) | Loading Unloading charge | 45 |  | 6 |  | 270
Transportation of filter media
f) | Transportation of easy load by per kg | 0 | Rs. per Kg
| Weight of sand @ 1600 kg/cu.m | 1600 | kg
| Total for transportation of 1 cu. m. aggregate |  |  |  |  | 0
g)'11-19 ka | Laying of the filter Gravel Media (Labour cost only)
| Skilled labour 0.65 nos. @ Rs 165 / no | 0.65 |  | 1225 |  | 796.25
|  | Sub Total for 1 cu. m. = |  |  | Rs. | 12561.25
| Contractor's overhead and value added tax @ | 29.95 | % |  | Rs. | 3762.09
Total Rate per cu.m of filter Gravel
| including material and labour with transportation |  |  |  | Rs. | 16323.34
11 | Filter Media (Gravel) [5 mm to 10mm]
Collection, seiving of the gravel through the wire mesh of required size to get the specified filter gravel and stocking with lead up to 10 m and then packing in jute bags
a) 3-2 ga | Collection, separation and lead up to 10 m for quarry capacity cum
| 5-20 mm size | 5.88 | md | 920 |  | 5409.6
b) 3-2 kha | Washing of gravel cum | 1.75 | md | 920 |  | 1610
c) | Packing of sieved gravel in jute bags L.S. | 0.5 | md | 920 |  | 460
d) | Cost of 45 jute bags for packing of 1 cum of sand @ Rs. 10.00 per piece | 45 |  | 5 |  | 225
e) | Loading Unloading charge @ 2.0/bag | 45 |  | 6 |  | 270
Transportation of filter media
f) | Transportation of easy load by per kg | 0 | Rs. per Kg
| Weight of sand @ 1600 kg/cu.m | 1600 | kg
| Total for transportation of 1 cu. m. aggregate |  |  |  |  | 0
g) '11-19 ka | Laying of the filter Gravel Media (Labour cost only)
| Skilled labour 0.65 nos. @ Rs 165 / no | 0.65 |  | 1225 |  | 796.25
|  | Sub Total for 1 cu. m. = |  |  | Rs. | 8770.85
| Contractor's overhead and value added tax @ | 29.95 | % |  | Rs. | 2626.87
Total Rate per cu.m of filter Gravel
| including material and labour with transportation |  |  |  | Rs. | 11397.72
12 | Filter Media (Gravel) [10 mm to 20 mm]
Collection, seiving of the gravel through the wire mesh of required size to get the specified filter gravel and stocking with lead up to 10 m and then packing in jute bags
a) 3-2 ga | Collection, separation and lead up to 10 m for quarry capacity cum
| 5-40 mm size | 4 | md | 920 |  | 3680
b) 3-2 kha | Washing of gravel cum | 1.75 | md | 920 |  | 1610
c) | Packing of sieved gravel in jute bags L.S. | 0.5 | md | 920 |  | 460
d) | Cost of 45 jute bags for packing of 1 cum of sand @ Rs. 10.00 per piece | 45 |  | 5 |  | 225
e) | Loading Unloading charge @ 2.0/bag | 45 |  | 6 |  | 270
Rate per Cu. M =
Transportation of filter media
f) | Transportation of easy load by per kg | 0 | Rs. per Kg
| Weight of sand @ 1600 kg/cu.m | 1600 | kg
| Total for transportation of 1 cu. m. aggregate |  |  |  |  | 0
g)'11-19 ka | Laying of the filter Gravel Media (Labour cost only)
| Skilled labour 0.65 nos. @ Rs 165 / no | 0.65 |  | 1225 |  | 796.25
|  | Sub Total for 1 cu. m. = |  |  | Rs. | 7041.25
| Contractor's overhead and value added tax @ | 29.95 | % |  | Rs. | 2108.85
Total Rate per cu.m of filter Gravel
| including material and labour with transportation |  |  |  | Rs. | 9150.1

## Ext. Mat_3
Rate Analysis for External Materials
WATER QUALITY IMPROVEMENT PROJECT
………………….. Project
Sn | Item | Unit | Unit Wt. | Transportation |  | Material Rate | Total | Remarks
|  |  | in | Rate | Amount | Without | Cost
|  |  | kg | Rs. | Rs. | VAT | Rs.
|  | 1 | 2 | 3 | (2 x 3) = 4 | 5 | 4 + 5
1 | Cement | Bag | 50 |  |  |  | 700
2 | M.S. Bar | kg | 1 |  |  |  | 99
3 | GI Wire 9 | kg | 1 | 0 | 0 | 124 | 124
4 | Salvage Wire 6 | kg | 1 | 0 | 0 | 92 | 92
5 | Bind Wire 12 | kg | 1 | 0 | 0 | 92 | 92
6 | Binding Wire | kg | 1 | 0 | 0 | 120 | 120
7 | CK Wire Mesh | Sqm. | 0.4 | 0 | 0 | 86 | 86
8 | Barbed Wire | kg | 1 | 0 | 0 | 115 | 115 |  | 16.4286
9 | Plain Wire | kg | 1 | 0 | 0 | 100 | 100
10 | GI Plain Sheet (26G) | Sqm. | 3.65 | 0 | 0 | 462.7057 | 462.7057
11 | Nails/Screws | kg | 1 | 0 | 0 | 132 | 132
12 | Polythene Sheet | Sqm. |  |  | 0 | 33 | 33
13 | Bitumen Paint | Lit. | 1 | 0 | 0 | 249.73 | 249.73
14 | Water Proof Cement Paint | kg | 1 | 0 | 0 | 38 | 38
15 | WPC Powder | kg | 1 | 0 | 0 | 117 | 117
16 | Fuel | Lit. | 1 | 0 | 0 | 147.79 | 147.79
17 | Cement Paint (Snowcem) | kg | 1 | 0 | 0 | 69 | 69
18 | Enamel Paint | Lit. | 1 | 0 | 0 | 534 | 534
19 | Primer | Lit. | 1 | 0 | 0 | 288 | 288
20 | GI Wire 8 - 10 | kg | 1 | 0 | 0 | 100.1 | 100.1
21 | GI Wire 12 | kg | 1 | 0 | 0 | 100.1 | 100.1
22 | M.S. Angle | kg | 1 | 0 | 0 | 93 | 93
23 | C. GI Sheet (26 Gauge) | Sqm. | 3.65 | 0 | 0 | 470.6286 | 470.6286 | 266.6667
24 | GI Sheet (26 Gauge) for ridge | rm. | 1 | 0 | 0 | 244.96 | 244.96
25 | 13mm dia Round Stand | m |  |  | 0 |  | 0
26 | Rope | m |  |  | 0 |  | 0
27 | Holdfast | No | 1 |  | 0 | 21.14 | 21.14
28 | Screw Nails | No | 1 |  | 0 | 2 | 2
29 | Hinge 150 mm | No | 1 |  | 0 | 59 | 59
30 | Tower bolt 150mm | No | 1 |  | 0 | 71 | 71
31 | Tower bolt 300mm | No | 1 |  | 0 | 114 | 114
32 | Nut & Bolts | kg | 1 | 0 | 0 | 12.18 | 12.18
33 | J-Hook | No | 1 |  | 0 | 17.125 | 17.125
34 | U-Hook | No |  |  | 0 | 17.125 | 17.125
35 | Bitumen Washer | No. | 1 |  | 0 | 3 | 3
36 | GI Wire Mesh | kg | 1 | 0 | 0 | 100 | 100
37 | Lockset 250 mm | No | 1 |  | 0 | 277 | 277
38 | Handle | No | 1 |  | 0 | 159 | 159
39 | Spring Set | No | 1 |  | 0 | 190 | 190
40 | Aluminium Paint | Lit. | 1 | 0 | 0 | 315 | 315
41 | GI Mesh Wire Screen | No |  |  | 0 | 85 | 85
42 | 10 mm Suspender Cable | m | 0.36 | 0 | 0 | 165 | 165
43 | 14 mm Suspender Cable | m | 0.7 | 0 | 0 | 165 | 165
44 | Flat Stone for Small Chamber | Set |  |  | 0 | 20 | 20
45 | Sand Paper | No |  |  | 0 | 6 | 6
46 | Tar Felt | Lit. | 1 | 0 |  | 140 | 140
47 | Bitumen | Lit. | 1 | 0 | 0 | 30 | 30
48 | Firewood | kg | 1 | 0 | 0 | 3 | 3
49 | Brick | No | 1 | 0 | 0 | 15.145 | 15.145
50
51
52
53 | Item | [5 empty] | Rate | Remarks
54 | Block Stone | [5 empty] | 2575.99
55 | Bond Stone | [5 empty] | 2575.99
56 | 40 mm Aggregate | [5 empty] | 3352.32
57 | 20 mm Aggregate | [5 empty] | 3352.32
58 | 10 mm Aggregate | [5 empty] | 3352.32
59 | Sand | [5 empty] | 3175.88
50 | Mud | cum |  |  |  |  | 343
51 | Sal Wood | cum |  |  |  |  | 214901.1917
52 | Local Wood | cum |  |  |  |  | 57400
53 | Bamboo | No |  |  |  |  | 240
54 | Skilled Labour (Mason) | Manday |  |  |  |  | 1225
55 | Unskilled Labour (Mason) | Manday |  |  |  |  | 920
56 | Skilled Labour (Painter) | Manday |  |  |  |  | 1225
57 | Unskilled Labour (Painter) | Manday |  |  |  |  | 920
58 | Skilled Labour (Plumber) | Manday |  |  |  |  | 1225
59 | Kaligad ( Juniour Plumber) | Manday |  |  |  |  | 920
60 | Skilled Labour (Carpenter) | Manday |  |  |  |  | 1225
61 | Unskilled Labour (Carpenter) | Manday |  |  |  |  | 920
62 | Unskilled Labour (Porter) | Manday |  |  |  |  | 920

## Rates
Shankharpur Municipality
Office of Municipal Executive
Summary of Rate Analysis for Water Supply and Irrigation For F/Y 2081/82
Sn. | Norms no | Items | Unit | Rate Per Unit ( without VAT ) | Reference No.
Earth Works
1 | 1-8 | Site clearance | m2 | 137.54 | F4
2 | 2-9 | Earthwork in Excavation in ordinary soil | m3 | 1089.74 | F5
3 | 2-12 | Earthwork in Excavation in hard soil | m3 | 1362.18 | F6
4 | 2-14 | Earthwork in Excavation in boulder mixed soil | m3 | 1732.69 | F7
5 | 2-15a | Earthwork in Excavation in soft rock | m3 | 3269.22 | F8
6 | 2-15b | Earthwork in Excavation in medium rock | m3 | 4903.83 | F9 | not available in other rate analysis
7 | 2-16b | Earthwork in Excavation in hard rock with chiselling | m3 | 27461.45 | F10
8 | 2-25a | Earthwork in backfilling in ordinary soil | m3 | 544.87 | F11
9 | 2-39c | Earthwork in backfilling with hard soil | m3 | 686.54 | F12
10 | 2-39d | Earthwork in backfilling with boulder mixed soil | m3 | 653.84 | F13
11 | 2-39e | Earthwork in backfilling with soft rock | m3 | 1198.71 | F14
Stone Works
11 | 6-5 | Stone soling work | m3 | 5141.87 | F16
12 | 11-16 | Stone Pitching with sand | m3 | 10963.48 | F17
13 | 6-2.1 | Dry stone masonry work | m3 | 6783.38 | F18
14 | 6-2.2 | Stone masonry in mud mortar | m3 | 7213.55 | F19
15 | 6-3.1 | R.R. masonry in 1:3 cement mortar | m3 | 15319.1 | F20
16 | 6-3.2 | R.R. masonry in 1:4cement mortar | m3 | 14865.17 | F21
17 | 6-3.3 | R.R. masonry in 1:6cement mortar | m3 | 14084.92 | F22
Brick Works
18 | 11-15(ka) | Flat brick soling | m2 | 1163.4 | F16
19 | 5-1(kha 2) | Chimney made Brick work in 1:4 cement mortar | m3 | 18942.74 | F17
20 | 5-1(kha 3) | Chimney made Brick work in 1:6 cement mortar | m3 | 18532.78 | F18
Concrete Works
21 | 7-2c | Plain cement concrete (1:3:6) in sub Structure | m3 | 14330.41 | F24
22 | 7-2d | Plain cement concrete (1:2:4) sub Structure | m3 | 15694.9 | F25
23 | 7-4 b | Plain cement concrete (1:1:5:3) sub Structure | m3 | 16948.41 | F26
24 | 7-2 d | Plain cement concrete (1:2:4) in super structure | m3 | 17740.76 | F27 | not available in other rate analysis
25 | 7-4 b | Plain cement concrete (1:1.5:3) in super structure | m3 | 18782.66 | F28
26 | 7-2d | Plain cement concrete (1:2:4) substructure with 2% WPC | m3 | 15709.63 | F29
27 | 7-4 b | Plain cement concrete (1:1:5:3) substructure with 2% WPC | m3 | 16966.81 | F30
Miscelleneous Works
28 | 7-5 | Mild steel reinforcement | kg | 123.56 | F32
29 | 8-2a | Form work for concrete work in simple slab and structure | m2 | 1278.27 | F33
|  | Form work for concrete work in arch,dome,etc ( Assuming form work canbe used 4 times) | m2 | 2395.08 | F34
30 | DWSS | HDPE pipe formwork for ferro-cement works | m2 | 459.51 | F35
31 | DWSS | Bar binding works including chicken wire, MS rods, GI plain wires etc | m2 | 1222.5 | F36
32 | 24-6 | Barbed wire fencing | m | 99.291 | F37
33 | 24-7 | Barbed wire fencing on wooden posts (2 diagonals & 5 horizontals) @ 3m c\c | m | 1426.8 | F38
34 | 10-17 | Wood works for door window frame | m3 | 326279.6 | F39
35 |  | 38 mm thick wooden shutter with 24 SWG plain sheet on one side | m2 | 17634.79 | F40
|  | 38 mm thick panelled wooden shutter | m2 | 10386.54 | F41
36 | 9-1 | CGI sheet roofing | m2 | 1052.2 | F42
37 | 9-2 | G.I plain sheet ridge work, collecting material all complete | rm | 965.21 | F42
38 |  | Laying of one layer of 500 G of Polythene sheet | m2 | 185.96 | F43
39 | 16-2a+14-5a | Making gabion boxes including cutting, wire, netting etc. and placing in site and tying all complete : Mesh size: hex. 100×120mm, Mesh wire-10SWG, selvedge wire-7 SWG) : size 2×1×1 m | no | 2649.54 | F44
40 | 16-11 | Filling of Gabion box with stone | m3 | 3787.63 | F45
41 |  | Gravel packing 20,25 mm dia | m3 | 5111.75 | F46
42 | 10-17 | Wood work for beams, rafters,etc. | m3 | 96024.08 | F47
43 | 10-19 | 25 mm thick eavesboard | m² | 2056.38 | F48
Plastering, Punning and Pointing works
44 | 12-1a | 12.5 mm thick 1:2 c-s plaster | m2 | 527.79 | F50
45 | 12-1b | 12.5 mm thick 1:3 c-s plaster | m2 | 485.7 | F51
46 | 12-1c | 12.5 mm thick 1:4 c-s plaster | m2 | 478.27 | F52
47 | 12-4a | 20 mm thick 1:3 c-s plaster | m2 | 624.02 | F53
48 | 12-4b | 20 mm thick 1:4 c-s plaster | m2 | 609 | F54
49 | 12-4c | 20 mm thick 1:6 c-s plaster | m2 | 575.84 | F55
| 12-1a | 12.5 mm thick 1:2 c-s plaster with 2% WPC | m2 | 528.21 | F56
| 12-1b | 12.5 mm thick 1:3 c-s plaster with 2% WPC | m2 | 486.67 | F57
| 12-4a | 20 mm thick 1:3 c-s plaster with 2% WPC | m2 | 624.2 | F58
50 | 13-10 | 3 mm thick 1:1 c-s punning | m2 | 332.33 | F59
51 | 14-2c | 1:3 c-s Flush ruled pointing work | m2 | 361.27 | F60
Painting Works
52 | 13-5 | Two coats of enamel painting with one coat of primer | m2 | 378.44 | F61
53 | 13-12b | Two coats snowcem painting | m2 | 200.01 | F62
54 | 13-10 | Two coats of bitumen painting | m2 | 97.89 | F63
Pipe Jointing Works
HDPE Pipes
55 | 17-2 | Laying and joining of 20,25 mmØ HDPE pipe with butt-weld joints | m | 4.88 | F65
56 | 17-2 | Laying and joining of 32 mmØ HDPE pipe with butt-weld joints | m | 6.02 | F66
57 | 17-2 | Laying and joining of 40,50 mmØ HDPE pipe with butt-weld joints | m | 7.32 | F67
58 | 17-2 | Laying and joining of 63-90 mmØ HDPE pipe with butt-weld joints | m | 96.87 | F68
| 17-2 | Laying and joining of 110,125 mmØ HDPE pipe with butt-weld joints | m | 142.69 | F69
| 17-2 | Laying and joining of 140-180 mmØ HDPE pipe with butt-weld joints | m | 188.52 | F70
59 | DWSS | Laying and joining of 200-250 mmØ HDPE pipe with butt-weld joints | m | 272.27 | F71
GI Pipes
60 | 17-4a | Laying and joining of 15,20 mmØ GI pipe with socket joints | m | 105.76 | F73
61 | 17-4a | Laying and joining of 25,32 mmØ GI pipe with socket joints | m | 145.44 | F74
62 | 17-4a | Laying and joining of 40,50 mmØ GI pipe with socket joints | m | 198.32 | F75
63 | 17-4a | Laying and joining of 65,80 mmØ GI pipe with socket joints | m | 264.41 | F76
| 17-4a | Laying and joining of 100 mmØ GI pipe with socket joints | m | 330.5 | F77
64 | 17-4a | Laying and joining of 125 mmØ GI pipe with socket joints | m | 403.22 | F78
64 | 17-4a | Laying and joining of 150 mmØ GI pipe with socket joints | m | 462.73 | F78
|  | Standard mild steel angle ( 25×25×3 mm size ) framed grill gate |  | 2025
|  | Supply and fixing of standard manhole cover ( 45×45 cm) |  | 1625.4
|  | Supply and fixing of standard manhole cover of 60cm diameter |  | 1479.6
|  | Supply and fixing of standard manhole cover ( 60×60 cm) |  | 2879.55
|  | Fly proof net fixing |  | 194.1975
Transportation work
65 |  | Convenient load from store to site | kg | 0 | F80
66 |  | Transportation of pipes and fittings from store to project site | kg | 0 | F81
Installation of pipes and fittins in structures:-
|  | Installation of pipes and fittings for spring intake | job | 600 | F83
|  | Installation of pipes and fittings for stream intake | job | 600 | F84
|  | Installation of pipes and fittings for ferrocement RVT | job | 1500 | F85
|  | Installation of pipes and fittings for collection chamber | job | 800 | F86
|  | Installation of pipes and fittings for distribution chamber | job | 800 | F87
|  | Installation of pipes and fittings for break pressure chamber/RVT for school | job | 800 | F88
|  | Installation of pipes and fittings for air valve chamber | job | 600 | F89
|  | Installation of pipes and fittings for valve chamber | job | 800 | F90
|  | Installation of pipes and fittings for public tap stand post | job | 600 | F91
|  | Installation of pipes and fittings for stream crossing | job | 800 | F92
|  | Installation of pipes and fittings for cable crossing | job | 1500 | F93
|  | Water diversion works in bed crossing | job | 1500 | F94
|  | Dewatering work in intake works | job | 450 | F95
|  | Supply and installation of water seal pan | job | 1184.5 | F96
|  | Supply and installation of wash basin | job | 1500 | F96
0

## Rate-1
Analysis of Rates
| Name of Scheme : |  | Sankhu Drinking Water Supply Project
Assumptions
| Density of sand |  |  |  |  | = |  | 1450 | kg/m³
| Density of rubble stone |  |  |  |  | = |  | 2000 | kg/m³
| Density of aggregate |  |  |  |  | = |  | 1600 | kg/m³
| Name of market : |  | Sankhu
| Name of roadhead : |  | Sankhu
Distance of project site from market on :
|  |  | - Foot |  |  | = |  | 0 | kosh
|  |  | - Earthen road |  |  | = |  | 0 | km
|  |  | - Gravel road |  |  | = |  | 0 | km
|  |  | - Metalled road |  |  | = |  | 0 | km
| Sand is available in |  | Sankhu
Distance of river from project site for sand collection
| for head load |  |  |  |  | = |  | 0 | km
If there is tractor/ truck road distance of haulage for sand transportation on :
|  |  | - Earthen road |  |  | = |  | 0 | km
|  |  | - Gravel road |  |  | = |  | 0 | km
|  |  | - Metalled road |  |  | = |  | 0 | km
| Distance of quarry from project site for stone / aggregate |  |  |  |  | = |  | 0 | km
| Cost of sand per m³ for purchase | [6 empty] | 0 | Rs.
District Rates :
| District rate of transportation by head load for : | [6 empty] | ma
| - convenient load |  |  |  | = |  |  | 1.6 | Rs./kg.kosh
| - inconvenient load as bars, ms angle, etc. |  |  |  | = |  |  | 2.72 | Rs./kg.kosh
| - GI & HDPE pipes | [6 empty] | 3.2 | Rs./kg.kosh
| District rate of transportation by truck for convenient load on : |  |  |  |  | Truck analysis
|  |  | - Earthen road |  | = |  |  | 6 | Rs./km.quintal
|  |  | - Gravel road |  | = |  |  | 3 | Rs./km.quintal
|  |  | - Metalled road |  | = |  |  | 1.75 | Rs./km.quintal
| District rate of transportation by truck for inconvenient load on : |  |  |  |  | Truck analysis
|  |  | - Earthen road |  | = |  |  | 9 | Rs./km.quintal
|  |  | - Gravel road |  | = |  |  | 4.5 | Rs./km.quintal
|  |  | - Metalled road |  | = |  |  | 2.63 | Rs./km.quintal
| Rate of load / unload |  |  |  | = |  |  | 21.5 | Rs./quintal
| District rate of Skilled labour |  |  |  | = |  |  | 1225 | Rs./d
| District rate of unskilled labour |  |  |  | = |  |  | 920 | Rs./d
| District rate of plumber |  |  |  | = |  |  | 920 | Rs./d
Rate of some local materials
1 | Sand for 1 m³ | [6 empty] | 3175.8797
| Distance from site to |  | Sankhu |  | = |  |  | 0 | km
| Labour required for collection, screening and stacking of river sand | [6 empty] | 0 | nos
| Labour required for transportation upto 13 km by headload | [6 empty] | 36.25 | nos
| Hence,Labour required for transportation upto site |  |  |  | 0 | km | = | 0 | nos
| Total labour required to collect and transport 1 m³ of sand upto site | [5 empty] | = | 0 | nos
| Cost of labour for collection and transportation | [6 empty] | 0
| Cost of transportation by truck |  | - Earthen road |  | 0 | km | = | 0
|  |  | - Gravel road |  | 0 | km | = | 0
|  |  | - Metalled road |  | 0 | km | = | 0
| Rate 1 m³ of sand at site ( transporation cost +collection or purchase cost) | [5 empty] | = | 3175.8797 | Rs.
2 | Stone for 1 m³
| If it is to be purchased, cost/m³ |  |  |  |  | = |  | 2575.9913
| Distance of quarry from site |  |  |  |  | = |  | 0 | km
| Labour required for collection and stacking of 1 m³ of stone |  |  |  |  | = |  | 1.4 | nos
| Cost of labour for collection and stacking of 1 m³ of stone |  |  |  |  | = |  | 0 | Rs.
| Cost of transportation of 1 m³ of stone up to site |  |  |  |  | = |  | 0 | Rs.
| Rate of 1 m³ of Stone at site |  |  |  |  | = |  | 2575.9913 | Rs.
3 | Aggregates (20-40 mm size) for 1m³
Labour required for breaking and stacking of 1 m³ of
| aggregate(15/2 nos) |  |  |  |  | = |  |  | nos. | 7.5
| Cost of labour for breaking and stacking of 1 m³ of aggregate |  |  |  |  | = |  | 0 | Rs.
| Cost of transportation of 1 m³ of aggregate up to site |  |  |  |  | = |  | 0
| Rate of 1 m³ aggregate |  |  |  |  | = |  | 0 | Rs.
4 | Aggregates (10-20 mm size) for 1m³
Labour required for breaking and stacking of 1 m³ of
| aggregate(21.5/2 nos) |  |  |  |  | = |  |  | nos. | 10.75
| Cost of labour for breaking and stacking of 1 m³ of aggregate |  |  |  |  | = |  | 0 | Rs.
| Cost of transportation of 1 m³ of aggregate up to site |  |  |  |  | = |  | 0
| Rate of 1 m³ aggregate |  |  |  |  | = |  | 0 | Rs.
5 | Rate of Transportation :
| Road type | Distance | Convenient | Inconvenient |  |  |  | GI & HDPE pipe
| - Earthen road | 0 | 0 | 0 |  |  |  | 0 | Rs/kg
| - Gravel road | 0 | 0 | 0 |  |  |  | 0 | Rs/kg
| - Metalled road | 0 | 0 | 0 |  |  |  | 0 | Rs/kg
| - For head load | 0 | 0 | 0 |  |  |  | 0 | Rs/kg
| Loading - unloading | [7 empty] | Rs/kg
| Rate of transportation per kg : |  | 0 | 0 | Rs/kg |  |  | 0 | Rs/kg
| Rate of transportation of inconvenient load with CO ( Without VAT ) | [6 empty] | 0 | Rs/kg
6 | Local Wood per 1 m³
| If it is to be purchased, cost/m³ |  |  |  | = |  |  | 57400 | Rs.
| District rate of sawing per cft. |  |  |  | = |  |  | 0 | Rs/cft.
| Royalty per cft |  |  |  | = |  |  | 0 | Rs/cft.
| Value Added Tax @ 10 % of royalty |  |  |  | = |  |  | 0 | Rs/cft.
| Sub total | [6 empty] | 0 | Rs/cft.
Asuming that prepared wood is 70% of trunk wood ,
| Total rate |  |  |  | = |  |  | 0 | Rs/cft.
| Transportation cost, per cft. |  |  |  | = |  |  | 0 | Rs/cft.
| Sub total |  |  |  | = |  |  | 0 | Rs/cft.
| Miscelleneous expenses @ 5% of subtotal |  |  |  | = |  |  | 0 | Rs/cft.
| Total cost of local wood for 1 cft |  |  |  | = |  |  | 0 | Rs.
| Rate of local wood per 1 m³ |  |  |  | = |  |  | 57400 | Rs/m³
7 | Salwood per 1 m³
| District rate of salwood, per m³ | [6 empty] | 214901.1917 | Rs/m³
8 | Mud [per m³]
| District rate of mud |  |  |  | = |  |  | 343 | Rs/m³
[ If ther is no specific district rate of mud, it will be obtained as "1.5×labour cost]

## MR
Unit Rate of Non-local Materials at Site
Sankhu Drinking Water Supply Project | [6 empty] | Rate of VAT
Sn | Item | Unit | Maket rate of material |  | Unit | Transportation cost |  | Rate of
|  |  | Without VAT | With VAT | weight | Rate | Amount | material at site
|  |  | Rs./unit | Rs./unit | kg | Rs. | Rs. | With VAT(Rs)
1 | 2 | 3 | 4 | 4/(1+Vat/100) = 5 | 6 | 7 | (6 x 7) =8 | 5+8
1 | Cement | Bag | 585 | 661.05 | 50 | 0 | 0 | 585
| Rate per kg | [6 empty] | 11.7
2 | M.S. Bar | kg | 90 | 101.7 | 1 | 0 | 0 | 90
3 | Binding Wire | kg | 120 | 135.6 | 1 | 0 | 0 | 120
4 | GI Plain Wire | kg | 124 | 140.12 | 1 | 0 | 0 | 124
5 | Nails | kg | 132 | 149.16 | 1 | 0 | 0 | 132
6 | Chicken wire mesh | m | 86 | 97.18 | 0.4 | 0 | 0 | 86
7 | Fly proof net | m² | 137 | 154.81 | 0.5 | 0 | 0 | 137
8 | M.S. Angle, kg | kg | 93 | 105.09 | 1.4 | 0 | 0 | 93
9 | Barbed wire 12 SWG | kg | 115 | 129.95 | 1 | 0 | 0 | 115
| Rate per metre ( Assuming weight per metre as 0.17 kg ) | [6 empty] | 19.55
10 | GI plain sheet ( 26 SWG ) | m2 | 462.7057 | 522.8575 | 4.5 | 0 | 0 | 462.7057
11 | CGI sheet ( 26 SWG ) | m2 | 470.6286 | 531.8103 | 5.1 | 0 | 0 | 470.6286
12 | Primer | L | 288 | 325.44 | 1 | 0 | 0 | 288
13 | Enamel Paint | L | 534 | 603.42 | 1 | 0 | 0 | 534
14 | Bitumen Paint | L | 249.73 | 282.1949 | 1 | 0 | 0 | 249.73
15 | Snowcem paint | kg | 69 | 77.97 | 1 | 0 | 0 | 69
16 | Polythene Sheet | m2 | 33 | 37.29 |  | 0 | 0 | 33
17 | Water proofing compound | kg | 117 | 132.21 | 1 | 0 | 0 | 117
18 | Fuel (Petrol) | L | 147.79 | 167.0027 | 1 | 0 | 0 | 147.79
19 | Holdfast | No | 21.14 | 23.8882 | 1 | 0 | 0 | 21.14
20 | Screw | No | 2 | 2.26 | 0.02 | 0 | 0 | 2
21 | Hinge 150 mm | No | 59 | 66.67 | 0.15 | 0 | 0 | 59
22 | Tower bolt 150mm | No | 71 | 80.23 | 0.15 | 0 | 0 | 71
23 | Tower bolt 300mm | No | 114 | 128.82 | 0.2 | 0 | 0 | 114
24 | Lockset 250 mm | No | 277 | 313.01 | 0.3 | 0 | 0 | 277
25 | Handle | No | 159 | 179.67 | 0.2 | 0 | 0 | 159
26 | Nut & Bolts | kg | 12.18 | 13.7634 | 0.1 | 0 | 0 | 12.18
27 | J-Hook | No | 17.125 | 19.3512 | 0.15 | 0 | 0 | 17.125
28 | U-Hook | No | 17.125 | 19.3512 | 0.1 | 0 | 0 | 17.125
29 | Bitumen Washer | No. | 3 | 3.39 | 0.01 | 0 | 0 | 3
30 | Water seal pan | set | 0 | 0 | 3 | 0 | 0 | 0
31 | MS angle grill gate, of 15 kg | No | 1500 | 1695 | 15 | 0 | 0 | 1500
32 | MS angle manhole cover 60×60cm | set | 2133 | 2410.29 | 13 | 0 | 0 | 2133
33 | MS angle manhole cover 60 cmØ | set | 1479.6 | 1671.948 | 11 | 0 | 0 | 1479.6
34 | MS angle manhole cover 45×45cm | set | 1625.4 | 1836.702 | 9 | 0 | 0 | 1625.4
35 | 10 mm Suspender Cable | m | 210.69 | 238.0797 | 0.62 | 0 | 0 | -
36 | 14 mm Suspender Cable | m | 268.15 | 303.0095 | 1.21 | 0 | 0 | -
37 | Cost of truck | no | 3164000 | 3575320 |  |  |  | 3164000
38 | Cost of tyre | no | 22400.25 | 25312.2825 |  |  |  | 22400.25
39 | H.S.D. | L | 65 | 73.45 |  |  |  | 65 | VAT is not considered
40 | Mobil | L | 580.26 | 655.6938 |  |  |  | 580.26
41 | Gear oil | L | 580.26 | 655.6938 |  |  |  | 580.26
42 | Grease | L | 640.15 | 723.3695 |  |  |  | 640.15
Unit Rate of Local Materials
and Labours
Sankhu Drinking Water Supply Project
Sn | Item | Unit | Rate
Local materials
1 | Block Stone | m3 | 2225.1497
2 | Bond Stone | m3 | 2225.1497
3 | 10 - 20 mm Aggregate | m3 | 6500
4 | 20 - 40 mm Aggregate | m3 | 6500
5 | Sand | m3 | 3766.11
6 | Mud ( 1.5md of coolie) | m3 | 1125
7 | Sal Wood | m3 | 214901.1917
8 | Local Wood | m3 | 57400
9 | Bamboo | no | 240
Labours
10 | Skilled labour ( for all works ) | md | 1030
11 | Unskilled labour ( for all works ) | md | 750
12 | Plumber | md | 1030
13 | Helper | md | 750
14 | Driver | md | 750
15 | Asistant to driver | md | 690

## Analysis (2)
Analysis of Item Rates
This rate analysis is based on the HMG/N approved Norms 2041 ( Including second revision )
Name of Project : | Sankhu Drinking Water Supply Project
A. Earthworks ( for 1 m³ ) and Site clearance ( for 1 m² )
Earthwork in excavation with 10m lead and 1.5 m lift in pipeline trench in :
Materials and labours | Unit | Rate Rs/unit | Hard soil (Norms No 2-12) |  | Boulder/Gravel mixedsoil (Norms No 2-14) |  | Ordinary Soil (Norms No 2-9) |  | Soft rock (Norms No 2-15a) |  | Medium rock (Norms No 2-15b)
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs.
Coolie | Rs/day | 920 | 1.25 | 1150 | 1.59 | 1462.8 | 1 | 920 | 3 | 2760 | 4.5 | 4140
Tools and plants | % |  | 3% | 34.5 | 3% | 43.88 | 3% | 27.6 | 3% | 82.8 | 3% | 124.2
Subtotal |  |  |  | 1184.5 |  | 1506.68 |  | 947.6 |  | 2842.8 |  | 4264.2
Contracror's Overhead | % | 15% |  | 177.68 |  | 226 |  | 142.14 |  | 426.42 |  | 639.63
Rate/m³ ( Without VAT ) |  |  |  | 1362.18 |  | 1732.68 |  | 1089.74 |  | 3269.22 |  | 4903.83
Earthwork in excavation with 10m lead and 1.5 m lift in pipeline trench in :
Materials and labours | Unit | Rate Rs/unit | Hard rock (Norms No. 2-16b)
|  |  | Quantity | Cost Rs.
Coolie | Rs/day | 920 | 25.2 | 23184
Tools and plants | % |  | 3% | 695.52
Subtotal |  |  |  | 23879.52
Contracror's Overhead | % | 15% |  | 3581.93
Rate/m³ ( Without VAT ) |  |  |  | 27461.45
Earthwork in back filling for pipe line trench with compaction in layers of 20cm with water sprinkling and site clearance
Materials and labours | Unit | Rate Rs/unit | Hard soil (Norms No 2-39c) |  | Boulder/Gravel mixed soil (Norms No 2-39d) |  | Ordinary Soil (Norms No ) |  | Soft rock (Norms No 2-39e) |  | Site clearance per m² N(1-8)
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs.
Coolie | Rs/day | 920 | 0.63 | 579.6 | 0.6 | 552 | 0.5 | 460 | 1.1 | 1012 | 0.16 | 147.2
Tools and plants | % |  | 3% | 17.39 | 3% | 16.56 | 3% | 13.8 | 3% | 30.36 |  | 0
Subtotal |  |  |  | 596.99 |  | 568.56 |  | 473.8 |  | 1042.36 |  | 147.2
Contracror's Overhead | % | 15% |  | 89.55 |  | 85.28 |  | 71.07 |  | 156.35 |  | 22.08
Rate/m³ ( Without VAT ) |  |  |  | 686.54 |  | 653.84 |  | 544.87 |  | 1198.71 |  | 169.28
B. Stone Works ( for 1m³ ) : With a lead of 30 m and upto height 5 m. | [12 empty] | B.1 Stone Works ( for 1m3 ) : With a lead of 30 m and upto height 5 m.
Materials and labours | Unit | Rate Rs/unit | Dry stone soling in foundation (N 6-5) |  | Dry stone masonary (N6-2a) |  | Stone masonary in mud mortar (N6- 2b) |  | RR Stone masonary in 1:4 cs mortar (N6-1b) |  | RR stone masonary in 1:6 cs mortar (N6-1c) |  | Materials and labours | Unit | Rate Rs/unit | Stone pitching with sand (N 11-16) |  | RR stone masonary in 1:3 cs mortar (N6-1c)
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. |  |  |  | Quantity | Cost Rs. | Quantity | Cost Rs.
Cement | kg | 11.7 | - |  | - |  | - |  | 159 | 1860.3 | 106 | 1240.2 | Cement | kg | 11.7 |  | 0 | 194 | 2269.8
Sand | m³ | 3175.8797 | - |  | - |  |  |  | 0.45 | 1429.15 | 0.47 | 1492.66 | Sand | m3 | 3175.8797 | 0.71 | 2254.87 | 0.42 | 1333.87
Block Stone | m³ | 2575.9913 | 1.2 | 3091.19 | 1.1 | 2833.59 | 1.1 | 2833.59 | 1.1 | 2833.59 | 1.1 | 2833.59 | Block Stone | m3 | 2575.9913 | 1.1 | 2833.59 | 1.1 | 2833.59
Mud | m³ | 1125 | - |  | - |  | 0.42 | 472.5 | - |  | - |  | Mud | m3 | 0 |  | 0 |  | 0
Mason | no | 1225 | - |  | 1 | 1225 | 1 | 1225 | 1.5 | 1837.5 | 1.5 | 1837.5 | Mason | No | 1225 | 1 | 1225 | 1.5 | 1837.5
Coolie | no | 920 | 1.5 | 1380 | 2 | 1840 | 2.25 | 2070 | 5 | 4600 | 5 | 4600 | Coolie | No | 920 | 3.5 | 3220 | 5 | 4600
Subtotal |  |  |  | 4471.19 |  | 5898.59 |  | 6601.09 |  | 12560.54 |  | 12003.95 | Subtotal |  |  |  | 9533.46 |  | 12874.76
Contracror's Overhead | % | 15% |  | 670.68 |  | 884.79 |  | 990.16 |  | 1884.08 |  | 1800.59 | Contracror's Overhead | % | 15% |  | 1430.02 |  | 1931.21
Rate/m³ ( Without VAT ) |  |  |  | 5141.87 |  | 6783.38 |  | 7591.25 |  | 14444.62 |  | 13804.54 | Rate/m ³ ( Without VAT ) |  |  |  | 10963.48 |  | 14805.97
C. Concrete work in substructure and super structure (for 1m³ ) | [12 empty] | C.1 Concrete work in substructure with 2% WPC(for 1m3 )
(With a lead of 30 m and all materials supplied ) | [12 empty] | (With a lead of 30 m and all materials supplied )
Materials and labours | Unit | Rate Rs/unit | P.C.C (1:3:6) work in sub structure (N 7-2c) |  | P.C.C (1:2:4) work in sub structure (N 7-2d) |  | P.C.C(1:1.5:3) work in sub structure ( N7-2d +N7-4b) |  | P.C.C1:2:4) work In superstructure (N 7-4a) |  | P.C.C(1:1.5:3) work In superstructure (N 7-4b) |  | Materials and labours | Unit | Rate Rs/unit | P.C.C (1:2:4) work in sub structure with 2% W.P.C(N 7-2d) |  | P.C.C(1:1.5:3) work in sub structure with 2% W.P.C ( N7-2d +N7-4b)
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. |  |  |  | Quantity | Cost Rs. | Quantity | Cost Rs.
Cement | kg | 11.7 | 220 | 2574 | 320 | 3744 | 400 | 4680 | 320 | 3744 | 400 | 4680 | Cement | kg | 11.7 | 320 | 3744 | 400 | 4680
Sand | m³ | 3175.8797 | 0.47 | 1492.66 | 0.445 | 1413.27 | 0.425 | 1349.75 | 0.445 | 1413.27 | 0.425 | 1349.75 | Sand | m3 | 3175.8797 | 0.445 | 1413.27 | 0.425 | 1349.75
Aggregate-10-20mm | m³ | 3352.32 |  |  | 0.33 | 1106.27 | 0.86 | 2883 | 0.33 | 1106.27 | 0.86 | 2883 | Aggregate-10-20mm | m3 | 3352.32 | 0.33 | 1106.27 | 0.86 | 2883
Aggregate-20-40mm | m³ | 3352.32 | 0.89 | 2983.56 | 0.52 | 1743.21 |  |  | 0.52 | 1743.21 |  |  | Aggregate-20-40mm | m3 | 3352.32 | 0.52 | 1743.21
W.P.C @2% | kg | 117 | [10 empty] | W.P.C @2% | Kg | 117 | 6.4 | 748.8 | 8 | 936
Skiled Labour | no | 1225 | 1 | 1225 | 1 | 1225 | 1 | 1225 | 0.8 | 980 | 0.8 | 980 | Skiled Labour | no | 1225 | 1 | 1225 | 1 | 1225
Coolie | no | 920 | 4 | 3680 | 4 | 3680 | 4 | 3680 | 7 | 6440 | 7 | 6440 | Coolie | no | 920 | 4 | 3680 | 4 | 3680
Subtotal |  |  |  | 11955.22 |  | 12911.75 |  | 13817.75 |  | 15426.75 |  | 16332.75 | Subtotal |  |  |  | 13660.55 |  | 14753.75
Contracror's Overhead | % | 15% |  | 1793.28 |  | 1936.76 |  | 2072.66 |  | 2314.01 |  | 2449.91 | Contracror's Overhead | % | 15% |  | 2049.08 |  | 2213.06
Rate/m ³ ( Without VAT ) |  |  |  | 13748.5 |  | 14848.51 |  | 15890.41 |  | 17740.76 |  | 18782.66 | Rate/m ³ ( Without VAT ) |  |  |  | 15709.63 |  | 16966.81
D. Steel reinforcement (kg), form work (m²) ,Ferrocement work(per m²), and wood work(per m³) for door-window frame etc. | [12 empty] | D.1 Form work (m2)
Materials and labours | Unit | Rate Rs/unit | Steel rein for cement cutting,bending &placing in place,etc,per kg (N7-5) |  | Shuttering work for slabs,etc(per m²) N8-2a |  | HDPE Formwork for ferrocement works per m² (DWSS-Standard) |  | Barbinding work for fe-c,including chicken wire,plain GI wire,M.S.bars etc. per m² (DWSS) |  | Wood work for door/ window frame per m³ N10-I7 |  | Materials and labours | Unit | Rate Rs/unit | Shuttering work for arch,dome,etc(per m2) N8-2a |  | staging work for culvert, bridge, dome, etc.(per m³) N15-31a |  | Wood work for beams, rafters,etc. per m³ N10-I7
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. |  |  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs.
Steel bar | kg | 90 | 1.05 | 94.5 | - |  |  |  | 2.593 | 233.37 |  |  | Nail | kg | 132 | 0.25 | 33 |  | 0 |  | 0
Binding wire | kg | 120 | 0.01 | 1.2 | - |  | 0.083 | 9.96 | 0.111 | 13.32 |  |  | Wood for formwork | m3 | 57400 | 0.0526/4x0.75 | 566.11 |  |  | 1.05
GI Plain wire | kg | 124 | - |  | - |  |  |  | 2.083 | 258.29 |  |  | Wood for scaffolding | m3 | 57400 | 0.075/4x0.75 | 807.19
Chicken wire | m | 86 | - |  | - |  |  |  | 1.806 | 155.32 |  |  | Skiled labour | no | 1225 | 0.26 | 318.5 | 0.5 | 612.5 | 0.5 | 612.5
Nail | kg | 132 | - |  | 0.25 | 33 | 0.014 | 1.85 |  |  |  |  | coolie | no | 920 | 0.389 | 357.88 | 0.5 | 460 | 0.5 | 460
Hold fast | no | 21.14 | [8 empty] | 92 | 1944.88
Screw | no | 0.5 | [8 empty] | 184 | 92
Wood | m³ | 57400 | - |  | 0.0526/4x0.75 | 452.89 |  |  |  |  | 1.1 | 63140 | Subtotal |  |  |  | 2082.68 |  | 1072.5 |  | 1072.5
Bamboo | no | 240 | - |  | - |  | 0.333 | 79.92 |  |  |  |  | Contracror's Overhead | % | 15% |  | 312.4 |  | 160.88 |  | 160.88
32mmf HDP pipe | m | - |  |  |  |  | 40 | [5 empty] | Rate/m² ( Without VAT ) |  |  |  | 2395.08 |  | 1233.38 |  | 1233.38
Skiled labour | no | 1225 | 0.012 | 14.7 | 0.172 | 210.7 | 0.167 | 204.58 | 0.25 | 306.25 | 34 | 41650
coolie | no | 920 | 0.012 | 11.04 | 0.257 | 236.44 | 0.111 | 102.12 | 0.083 | 76.36 | 3.4 | 3128
Subtotal |  |  |  | 121.44 |  | 933.03 |  | 398.43 |  | 1042.91 |  | 109954.88
Contracror's Overhead | % | 15% |  | 18.22 |  | 139.95 |  | 59.76 |  | 156.44 |  | 16493.23
Rate / Unit ( Without VAT ) |  |  |  | 139.66 |  | 1072.98 |  | 458.19 |  | 1199.35 |  | 126448.11
E. Plastering Work (for 1m²) | [12 empty] | E.1 Plastering Work with 2% WPC (for 1m2)
Materials and labours | Unit | Rate Rs/unit | 12.5mm thick 1:2 c-s plaster( N12-1a) |  | 12.5mm thick 1:3 c-s plaster (N12-1b) |  | 12.5mm thick 1:4 c-s plaster (N12-1c) |  | 20mm 1:3 c-s plaster (N12-4a) |  | 20mm 1:4 c-s plaster (N12-4b) |  | Materials and labours | Unit | Rate Rs/unit | 12.5mm thick 1:2 c-s plasterwith 2% W.P.C ( N12-1a) |  | 12.5mm thick 1:3 c-s plaster with 2% W.P.C(N12-1b) |  | 20mm 1:3 c-s plaster with 2% W.P.C (N12-4a) |  | 20mm 1:6 c-s plaster (N12-4c)
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. |  |  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs.
Cement | kg | 11.7 | 9 | 105.3 | 6.25 | 73.13 | 5.38 | 62.95 | 9.6 | 112.32 | 8.1 | 94.77 | Cement | kg | 11.7 | 9 | 105.3 | 6.25 | 73.13 | 9.6 | 112.32 | 5.7 | 66.69
Sand | m3 | 3175.8797 | 0.0122 | 38.75 | 0.0128 | 40.65 | 0.0146 | 46.37 | 0.0195 | 61.93 | 0.022 | 69.87 | Sand | m3 | 3175.8797 | 0.0122 | 38.75 | 0.0128 | 40.65 | 0.0195 | 61.93 | 0.0235 | 74.63
W.P.C. | kg | 117 | [10 empty] | W.P.C. | kg | 117 | 0.18 | 21.06 | 0.13 | 15.21 | 0.19 | 22.23 |  | 0
Skilled labour | no | 1225 | 0.12 | 147 | 0.12 | 147 | 0.12 | 147 | 0.14 | 171.5 | 0.14 | 171.5 | Skilled labour | no | 1225 | 0.12 | 147 | 0.12 | 147 | 0.14 | 171.5 | 0.14 | 171.5
Coolie | no | 920 | 0.16 | 147.2 | 0.16 | 147.2 | 0.16 | 147.2 | 0.19 | 174.8 | 0.19 | 174.8 | Coolie | no | 920 | 0.16 | 147.2 | 0.16 | 147.2 | 0.19 | 174.8 | 0.19 | 174.8
Subtotal |  |  |  | 438.25 |  | 407.98 |  | 403.52 |  | 520.55 |  | 510.94 | Subtotal |  |  |  | 459.31 |  | 423.19 |  | 542.78 |  | 487.62
Contracror's Overhead | % | 15% |  | 65.74 |  | 61.2 |  | 60.53 |  | 78.08 |  | 76.64 | Contracror's Overhead | % | 15% |  | 68.9 |  | 63.48 |  | 81.42 |  | 73.14
Rate/m² ( Without VAT ) |  |  |  | 503.99 |  | 469.18 |  | 464.05 |  | 598.63 |  | 587.58 | Rate/m² ( Without VAT ) |  |  |  | 528.21 |  | 486.67 |  | 624.2 |  | 560.76
F . Pointing ,Punning ,Barbed wire fencing, C.G.I. sheet roofing
Materials and labours | Unit | Rate Rs/unit | 3mm 1:1 c-s Punning (for 1m²) (N14 -6) |  | 1:3 c-s Flush ruled Pointing (m²) (N14 -26) |  | G.I barbed wire fencing (1m) N24 -6 |  | G.I barbed wire fencing on wooden posts (5 horz.,2 diagonals)@3mc/c for 1m |  | C.G.Isheet roofing (1m²) N -9 -1
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs.
Cement | kg | 11.7 | 3.36 | 39.31 | 3.06 | 35.8
Sand | m3 | 3175.8797 | 0.0023 | 7.3 | 0.0063 | 20.01
GI Barbed wire | m | 19.55 | - |  |  |  | 1.1 | 21.51 | 8.333 | 162.91
Local wood | m3 | 57400 | [6 empty] | 0.006 | 344.4
CGI sheet-26G | m2 | 470.6286 | - | [7 empty] | 1.2 | 564.75
Nuts & bolts | no | 12.18 | - | [7 empty] | 3 | 36.54
J - hook | no | 17.125 | - | [7 empty] | 2.5 | 42.81
U - hook | no | 2 |  |  |  |  | LS | 2.151 | 2.567 | 5.13
Skilled labours | no | 1225 | 0.1 | 122.5 | 0.1 | 122.5 | 0.01076 | 13.18 | 0.033 | 40.43 | 0.11 | 134.75
Collies | no | 920 | 0.1 | 92 | 0.14 | 128.8 | 0.0538 | 49.5 | 0.067 | 61.64 | 0.125 | 115
Subtotal |  |  |  | 261.11 |  | 307.11 |  | 86.341 |  | 614.51 |  | 893.85
Contracror's Overhead | % | 15% |  | 39.17 |  | 46.07 |  | 12.95 |  | 92.18 |  | 134.08
Rate / Unit ( Without VAT ) |  |  |  | 300.28 |  | 353.18 |  | 99.291 |  | 706.69 |  | 1027.93
G. Enamel & Bitumen Paints and white washing (For 1m²)
Materials and labours | Unit | Rate Rs/unit | Two coats of enamel paint N-13-5 |  | Two coats of Bitumen paint N-13-10 |  | Two coats of Snowcem paint N-13-12 |  | Making gabion boxes including cutting, wire, netting etc. and placing in site and tying all complete : Mesh size: hex. 100×120mm, Mesh wire-10SWG, selvedge wire-7 SWG) : size 2×1×1 m(N 16-05a+14-05a) |  | Filling of Gabion crate with block stone for 1 m3
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs.
Primer | L | 288 | 0.081 | 23.33
Enamel | L | 534 | 0.16 | 85.44
Bitumen | L | 249.73 | - |  | 0.19 | 47.45
Snowcem | L | 69 | - |  |  |  | 0.5 | 34.5
GI Plain wire (10 SWG) | kg | 124 | [6 empty] | 24.15 | 2994.6
Selvage wire (7 SWG) | kg | 124 | [6 empty] | 3.15 | 390.6
Tying wire (12 SWG) | kg | 124 | [6 empty] | 0.95 | 117.8
Block Stone | m³ | 2575.9913 | [8 empty] | 1.1 | 2833.59
Skilled labours | no | 1225 | 0.12 | 147 | 0.04 | 49 | 0.065 | 79.63 | 0.45 | 551.25
Collies | no | 920 | 0.08 | 73.6 | 0.03 | 27.6 | 0.065 | 59.8 | 0.6 | 552 | 0.5 | 460
Subtotal |  |  |  | 329.37 |  | 124.05 |  | 173.93 |  | 4606.25 |  | 3293.59
Contracror's Overhead | % | 15% |  | 49.41 |  | 18.61 |  | 26.09 |  | 690.94 |  | 494.04
Rate/m² ( Without VAT ) |  |  |  | 378.78 |  | 142.66 |  | 200.02 |  | 5297.19 |  | 3787.63
H. HDPE Pipe Jointing (For 1m) Norms No 17 - 2 | [12 empty] | H.1 HDPE Pipe Jointing (For 1m) Norms No 17 - 2
Materials and labours | Unit | Rate Rs/unit | 20,25mm dia HDPE For (1000m) |  | 32 mm dia HDPE For (1000m) |  | 40,50mm dia HDPE For (1000m) |  | 63,75,90 mm dia HDPE For (50m) |  | 110,125 mm dia HDPE For (50m) |  | Material and labour | Unit | Rate Rs/unit | 140-180 mm dia HDPE For (50m) |  | 200-250 mm dia HDPE For (50m)
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. |  |  |  | Quantity | Cost Rs. | Quantity | Cost Rs.
Plumber | no. | 920 | 1 | 920 | 1 | 920 | 1.5 | 1380 | 1 | 920 | 1.5 | 1380 | Plumber | no. | 920 | 2 | 1840 | 3 | 2760
Helper | no. | 920 | 1 | 920 | 1 | 920 | 1.5 | 1380 | 1 | 920 | 1.5 | 1380 | Helper | no. | 920 | 2 | 1840 | 3 | 2760
Coolis | no. | 920 | 2 | 1840 | 3 | 2760 | 3 | 2760 | 2 | 1840 | 3 | 2760 | Coolis | no. | 920 | 4 | 3680 | 6 | 5520
Sub total |  |  | - | 3680 |  | 4600 |  | 5520 |  | 3680 |  | 5520 | Sub total |  |  |  | 7360 |  | 11040
Contingencies |  | 2.5% |  | 92 |  | 115 |  | 138 |  | 92 |  | 138 | Contingencies |  | 2.5% |  | 184 |  | 276
Tools & plants | day | 150 | 1 | 150 | 1 | 150 | 1 | 150 | 1 | 150 | 1 | 150 | Tools & plants | day | 150 | 2 | 300 | 2 | 300
Petrol | L | 147.79 | 0.25 | 36.95 | 0.25 | 36.95 | 0.25 | 36.95 | 0.5 | 73.9 | 0.5 | 73.9 | Petrol | L | 147.79 | 1 | 147.79 | 1.5 | 221.69
Subtotal |  |  |  | 3958.95 |  | 4901.95 |  | 5844.95 |  | 3995.9 |  | 5881.9 | Total |  |  |  | 7991.79 |  | 11837.69
Contracror's Overhead | % | 15% |  | 593.84 |  | 735.29 |  | 876.74 |  | 599.39 |  | 882.29 | C.P&VAT |  | 15% |  | 1198.77 |  | 1775.65
Grand Total |  |  |  | 4552.79 |  | 5637.24 |  | 6721.69 |  | 4595.29 |  | 6764.19 | Grand Total |  |  |  | 9190.56 |  | 13613.34
Rate /m |  |  |  | 4.55 |  | 5.64 |  | 6.72 |  | 91.91 |  | 135.28 | Rate /m |  |  |  | 183.81 |  | 272.27
I. GI Pipe jointing work (For 1m) N - 17- 4 a | [12 empty] | I.1 GI Pipe jointing work (For 1m) N - 17- 4 a
Materials and labours | Unit | Rate Rs/unit | 15,20 mm dia GI For (30m) |  | 25,32 mm dia GI For (30m) |  | 40,50mm dia GI For (30m) |  | 65,80 mm dia GI For (30m) |  | 100 mm dia GI For (30m) |  | Material and labour | Unit | Rate Rs/unit | 125 mm dia GI For (30m)
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. |  |  |  | Quantity | Cost Rs.
Plumber | no. | 920 | 0.5 | 460 | 0.5 | 460 | 0.75 | 690 | 1.25 | 1150 | 1.75 | 1610 | Plumber | no. | 920 | 2 | 1840
Helper | no. | 750 | 1 | 750 | 1.5 | 1125 | 2 | 1500 | 2 | 1500 | 2 | 1500 | Helper | no. | 920 | 2.5 | 2300
Coolis | no. | 920 | 1 | 920 | 1.5 | 1380 | 2 | 1840 | 3 | 2760 | 4 | 3680 | Coolis | no. | 920 | 5 | 4600
Sub total |  |  |  | 2130 |  | 2965 |  | 4030 |  | 5410 |  | 6790 | Subtotal |  |  |  | 8740
Red lead , Hemp etc. |  | 10% |  | 213 |  | 296.5 |  | 403 |  | 541 |  | 679 | Red lead , Hemp etc. |  | 10% |  | 874
Contingencies |  | 2.5% |  | 53.25 |  | 74.13 |  | 100.75 |  | 135.25 |  | 169.75 | Contingencies |  | 2.5% |  | 218.5
Subtotal |  |  |  | 2396.25 |  | 3335.63 |  | 4533.75 |  | 6086.25 |  | 7638.75 | Total |  |  |  | 9832.5
Contracror's Overhead | % | 15% |  | 359.44 |  | 500.34 |  | 680.06 |  | 912.94 |  | 1145.81 | C.P |  | 15% |  | 1474.88
Grand Total |  |  |  | 2755.69 |  | 3835.97 |  | 5213.81 |  | 6999.19 |  | 8784.56 | Grand Total |  |  |  | 11307.38
Rate /m |  |  |  | 91.86 |  | 127.87 |  | 173.79 |  | 233.31 |  | 292.82 | Rate /m |  |  |  | 376.91
J. Gravel Packing and door shutter
Materials and labours | Unit | Rate Rs/unit | Gravel packing for 1 m3 |  | 38 mm thick wooden shutter with GI plain sheet for 1 m2 [ Norms no 10-9) |  | 38 mm thick panelled wooden shutter for 1 m2 [ Norms no 10-2) |  | Wood work for beams, rafters,etc. per m³ N10-I7 |  | 25 mm thick eavesboard. per m² N10-I9
|  |  | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs. | Quantity | Cost Rs.
Aggregate - 40mm | m3 | 0 | 1.05 | 0 | - |  | - |  | - |  | -
Local wood | m3 | 57400 |  |  | 0.016748 | 961.35 | 0.039735 | 2280.79 | 1.05 | 60270 | 0.0275 | 1578.5
Nails | kg | 132 | - |  | LS | 5 | LS | 5 | LS | 50 | LS | 25
Hinges | no | 59 | - |  | 1.3363 | 78.84 | 2.8382 | 167.46 |  | 0 |  | 0
Locking set | no | 277 | - |  | 0.44543 | 123.39 | 0.47304 | 131.03 |  | 0 |  | 0
Tower bolt 150mm | no | 71 | - |  | 0.89087 | 63.25 | 0.94607 | 67.17 |  | 0 |  | 0
Handle | no | 159 | - |  | 0.44543 | 70.82 | 0.94607 | 150.43 |  | 0 |  | 0
GI plain sheet | no | 462.7057 |  |  | 2.0713 | 958.39 |  | 0 |  | 0 |  | 0
Skilled labour | no | 1225 | 1 | 1225 | 3.118 | 3819.6 | 4.7304 | 5794.7 | 17.6 | 21560 | 0.14 | 171.5
Collies | no | 920 | 3.5 | 3220 | 0.3118 | 286.86 | 0.47304 | 435.19 | 1.76 | 1619.2 | 0.0143 | 13.16
Total |  |  |  | 4445 |  | 6367.5 |  | 9031.77 |  | 83499.2 |  | 1788.16
C.P&VAT |  | 15% |  | 666.75 |  | 955.13 |  | 1354.77 |  | 12524.88 |  | 268.22
Rate /Unit |  |  |  | 5111.75 |  | 7322.63 |  | 10386.54 |  | 96024.08 |  | 2056.38

## reservoir 200 (hidden)
Shankharapur Municipaltiy Office
Office of Municipal Executuve
Bagmati Pradesh, Sankhu Kathmandu
Bill No: Final Bill
Contractor Name: SMO/079/80/84
Contractor's Name: Goldenstar Construction and Suppliers pvt. Ltd. ,Madhyapur thimi-3
Project: Construction of semi underground water tanks and sedimentaion tanks, Manichood Khanepani | [10 empty] | F/Y: 079/80
Location: Shankharapur-8 | [10 empty] | Date: 2079/8/25
S | DESCRIPTION | No | Rad. | L | B | H | QNTTY | Unit | Rate | Amount | norms
N |  |  | (m) | (m) | (m) | (m) |  |  | Rs | Rs | no.
| Wall Height = | 3 |  |  | 200 |  |  |  |  | Wall Thickness = | 0.2
| Inside Dia. = | 10.5 |  | (Gross Volume = |  | 230.9306 | Cum) |  |  | Dome Height = | 1.71
1 | Site Clearance | 1 | 10.5 |  |  |  | 346.3606 | job | 137.54 | 47638.4356 | LS
#REF!
2 | Excavation work Soft soils
| VC | 1 |  | 3.2 | 2 | 1.5 | 9.6
| Tank | 1 | 5.95 |  |  | 1.5 | 166.8304
| washout pipe trench | 1 |  | 10 | 0.6 | 0.9 | 5.4
[7 empty] | 181.8304 | m3 | 1089.74 | 198147.8066 | 2.14 |  | #REF!
3 | Back filling with loose soils | 1 |  |  |  | 1.1 | 29.4171 | m3 | 544.87 | 16028.4889 | 2.39a |  | #REF!
4 | Boulder Soling with sand
| VC | 1 |  | 3.2 | 2 | 0.15 | 0.96
| Tank | 1 | 5.95 |  |  | 0.2 | 22.244
[7 empty] | 23.204 | m3 | 5141.87 | 119312.192 | 6.5a |  | #REF!
4 | RRM in 1:6 c/s mortar in VC
| vc | 1 |  | 7.8 | 0.45 | 2 | 7.02
[7 empty] | 7.02 | m3 | 14084.92 | 98876.1384 | 6.1c |  | #REF!
1 | PCC(1:3:6) work as Lean Concrete for floor | 1 | 5.75 |  |  | 0.1 | 10.3869 | m3 | 14330.41 | 148848.4025 | 7.2c |  | #REF!
2 | PCC (1:2:4) in RCC components
| cover slab of VC | 2 |  | 3.2 | 2 | 0.1 | 1.28
[7 empty] | 1.28 | m3 | 15694.9 | 20089.472 | 7.2c |  | #REF!
3 | PCC (1:1.5:3) for RCC components with 2 % WPC
| Base slab | 1 | 5.75 |  |  | 0.3 | 31.1607
| Circular wall | 1 | 5.45 |  |  | 3 | 20.546
| Haunch at base | 0.5 |  | 31.7301 | 0.2 | 0.2 | 0.6346
| Circular dome beam | 1 |  | 34.2434 | 0.3 | 0.2 | 2.0546
| Conical roof slab | 1 | 5.45 |  |  |  | 19.5597
| Deduction for Manhole cover | 1 | 0.3 |  |  |  | -0.056549
[7 empty] | 73.899 | m3 | 16966.81 | 1253831.0863 | 7.4b1 |  | #REF!
4 | Formwork for concreting work
| bottom of cover slab of VC | 1 |  | 2.4 | 1.65 |  | 3.96
| sides of cover slab of VC | 1 |  | 7.2 |  | 0.1 | 0.72
| sides of base slab of tank | 1 | 5.75 | 36.1283 |  | 0.3 | 10.8385
| tank walls | 2 | 5.75 | 36.1283 |  | 3 | 216.7699
| soffit of conical roof slab | 1 | 5.25 |  |  |  | 91.0676
| deduction for MH cover | 1 | 0.3 |  |  |  | -0.28274
[7 empty] | 323.0732 | m2 | 1278.27 | 412974.7775 | 8.2a |  | #REF!
5 | Scafolding work | [5 empty] | 1 | job | 25000 | 25000 | LS |  | 75000
6 | Reinforcement work in RCC components |  |  |  |  | kg/m
(1) | 12mm @ 170 c/c both ways on both faces of base slab" | 247.0588 |  | 7.8736 |  | 0.89 | 1731.2709 | 0.17
(2) | 12mm vertical bars 160 c/c b/s upto 1.0m height" | 412.5 |  | 1.5 |  | 0.89 | 550.6875 | 0.16
(3) | 12mm vertical bars @ 160 c/c b/s for walls-long" | 412.5 |  | 3.5 |  | 0.89 | 1284.9375 | 0.16
(4) | 12mm circular hoop bars @ 150 c/c upto 1m height" | 6 |  | 34.2434 |  | 0.89 | 182.8595 | 0.15
(5) | 12mm inclined bars @ 160 c/c for base haunch" | 219 |  | 0.9 |  | 0.89 | 175.419 | 0.16
(6) | 12mm circular hoop bars @ 170 c/c 1m to 3m height" | 11 |  | 34.2434 |  | 0.89 | 335.2425 | 0.17
(7) | 8mm @ 150 c/c stirrups for beam" | 234.5723 |  | 1 |  | 0.395 | 92.656 | 0.15
(8) | 12mm bars 8 nos for circular beam" | 8 |  | 35.1858 |  | 0.89 | 250.5232 | 0.18
(9) | 12mm radial arc bars @ 150 c/c for conical roofslab" | 219 |  | 5.5215 |  | 0.89 | 1076.1892 | 0.15
(10) | 12mm circular bars @ 160 c/c for conical roof slab" | 34 |  | 18.0642 |  | 0.89 | 546.6214 | 0.16
(11) | 6mm Spacer bars(seperators)" | 96 |  | 0.5 |  | 0.22 | 10.56 | 0.5
(12) | 8mm @ 150 c/c both ways for VC" | 22.6667 |  | 1.5 |  | 0.395 | 13.43 | 0.15
[7 empty] | 6250.3967 | Kg | 123.56 | 772299.0131 | 7.5 |  | #REF!
7 | 12.5mm inside plaster in 1:3 c/s mortar with 2% WPC
| inner face of tank wall | 1 | 5.25 |  |  | 3 | 98.9602
| floor | 1 | 5.25 |  |  |  | 86.5901
[7 empty] | 185.5503 | m2 | 486.67 | 90301.7723 | 12.1a |  | #REF!
8 | 12.5mm outside plaster in 1:4 c/m
| outer face of tank wall | 1 | 5.65 |  |  | 3 | 106.5
| conical roof, both faces | 2 | 5.45 |  |  |  | 195.597
| deduction for MH opening | 2 | 0.3 |  |  |  | -0.56549
[7 empty] | 301.5315 | m2 | 478.27 | 144213.492 | 12.1c |  | 299497.4381
9 | 3mm punning with 1:1 c/s mortar
| floor portion | 1 | 5.25 |  |  |  | 86.5901
| inner face of wall | 1 | 5.25 |  |  | 3 | 98.9602
[7 empty] | 185.5503 | m2 | 332.33 | 61663.9366 | 11.20 |  | #REF!
10 | Double coat Snowcem paint on exposed surface
| outer face of wall | 1 | 5.65 |  |  | 1.5 | 53.25
| conical roof | 1 | 5.65 |  |  | 2.1 | 104.78
[7 empty] | 158.03 | m2 | 200.01 | 31607.5857 | 13.4b |  | 330.2463
11 | 2 coats bitumen painting over unexposed surface
| floor portion | 1 | 5.25 |  |  |  | 86.5901
| inner face of wall | 1 | 5.25 |  |  | 3 | 98.9602
[7 empty] | 185.5503 | m2 | 97.89 | 18163.5204 | 13.10b
12 | Supply and installation of outer and inner steel | 2 |  |  |  |  | 2 | set | 15000 | 30000 | LS
pipe ladders as directed by site Engineer
#REF! | 60 cm dia. MS MH cover including procuring | 3 |  |  |  |  | 3 | set | 3222 | 9666 | mh60
transporting and fixing at place,
#REF! | Installation of Pipe fittings | 1 |  |  |  |  | 1 | job | 15000 | 15000 | LS
#REF! | Construction site cleareance, leak proof test | 1 |  |  |  |  | 1 | job | 15000 | 15000 | LS
and disinfection of reservoir all complete
3528662.1199
B | Supply of Fittings for inlet, outlets,washout & overflow as per drawing, instruction and standard specification
2-1/2" Dia outlet -3 Nos
| 2-1/2" Dia 2m long G.I. Nipple | [5 empty] | 2 | pc | 3896 | 7792
| 2-1/2" Dia G.I. Nipple 30cm long | [5 empty] | 2 | pc | 1022 | 2044 |  | 4"
| 2-1/2" Dia G.I.Socket | [5 empty] | 1 | pc | 554 | 554
| 2-1/2" Dia G.I. Elbow | [5 empty] | 2 | pc | 805 | 1610
| 2-1/2" Dia G.I. Strainer50 cm long | [5 empty] | 2 | pc | 1774 | 3548
| 2-1/2" Dia Sluice valve | [5 empty] | 2 | pc | 11406 | 22812
| 2-1/2" Dia G.I. Flange | [5 empty] | 2 | set | 1699 | 3398
| 2-1/2" Dia G.I. /HDPE Flange | [5 empty] | 2 | set | 1824 | 3648
| 2-1/2" Dia C.I. Plug . | [5 empty] | 2 | pc | 214 | 428
| 2-1/2"*3/4" GI Unequal Tee | [5 empty] | 1 | pc | 1160 | 1160
| 3/4" GI nipple 2m long | [5 empty] | 2 | pc | 1271 | 2542
| 3/4" GI nipple 1 m long | [5 empty] | 1 | pc | 885.5 | 885.5
| 3/4" GI nipple 0.35 m long | [5 empty] | 1 | pc | 634.925 | 634.925
| 3/4"GI elbow | [5 empty] | 4 | pc | 94 | 376
| 3/4"GI Socket | [5 empty] | 2 | pc | 73 | 146
| 3/4"GIUnion | [5 empty] | 1 | pc | 238 | 238
| 3/4" short nipple 4" | [5 empty] | 3 | pc | 74 | 222
3" Dia overflow
| 3" Dia 2m long G.I. Nipple | [5 empty] | 2 | pc | 4645 | 9290
| 3" Dia G.I. Nipple 0.6 m long | [5 empty] | 1 | pc | 2093.5 | 2093.5
| 3" Dia G.I. Elbow | [5 empty] | 2 | pc | 1253 | 2506
| 3" Dia G.I. Socket | [5 empty] | 1 | pc | 817 | 817
| 3" Dia G.I. Plug . | [5 empty] | 1 | pc | 437 | 437
| 3" Dia G.I/HDPE.Flange Set. | [5 empty] | 1 | Set | 1950 | 1950
1-1/2" Dia Inlet - 1 No.
| 1-1/2" Dia 2m long G.I. Nipple | [5 empty] | 1 | pc | 2295 | 2295
| 1-1/2" Dia G.I. Nipple 1m long | [5 empty] | 1 | pc | 1447.5 | 1447.5
| 1-1/2" Dia G.I. Elbow | [5 empty] | 1 | pc | 308 | 308
| 1-1/2" Dia G.I. Socket | [5 empty] | 1 | pc | 208 | 208
| 1-1/2"Dia G.I. Short nipple | [5 empty] | 3 | pc | 116 | 348
| 1-1/2" Dia gate Valve | [5 empty] | 1 | pc | 3467 | 3467
| 1-1/2"Dia G.I. Plug . | [5 empty] | 1 | pc | 124 | 124
| 1-1/2" Dia G.I/HDPE.Flange Set. | [5 empty] | 2 | pc | 1332 | 2664
3" Dia Washout
| 3" Dia 2.8 m long G.I. Nipple | [5 empty] | 1 | Pc | 6103 | 6103
| 3" Dia Sluice valve | [5 empty] | 0 | pc | 13691 | 0
| 3" Dia G.I. Elbow | [5 empty] | 1 | pc | 1253 | 1253
| 3" Dia MS. Flange | [5 empty] | 2 | set | 1950 | 3900
| 3" Dia G.I. Plug . | [5 empty] | 1 | pc | 437 | 437
| 3" Dia G.I./HDPE Flange Set. | [5 empty] | 1 | set | 1950 | 1950
[9 empty] | Total | 93636.425 | Rs
3622298.5449

## reservoir 150 (hidden)
Shankharapur Municipaltiy Office
Office of Municipal Executuve
Bagmati Pradesh, Sankhu Kathmandu
Detail Measurement Sheet
Bill No: Final Bill
Contractor Name: SMO/079/80/84
Contractor's Name: Goldenstar Construction and Suppliers pvt. Ltd. ,Madhyapur thimi-3
Project: Construction of semi underground water tanks and sedimentaion tanks, Manichood Khanepani | [10 empty] | F/Y: 079/80
Location: Shankharapur-8 | [10 empty] | Date: 2079/8/25
S | DESCRIPTION | No | Rad. | L | B | H | QNTTY | Unit | Rate | Amount | norms
N |  |  | (m) | (m) | (m) | (m) |  |  | Rs | Rs | no.
| Wall Height = | 3 |  |  | 150 |  |  |  |  | Wall Thickness = | 0.2
| Inside Dia. = | 8.6 |  | (Gross Volume = |  | 174.2641 | Cum) |  |  | Dome Height = | 1.48
1 | Site Clearance | 1 | 8.6 |  |  |  | 232.3522 | job | 137.54 | 31957.7206 | LS
2 | Excavation work in BMS soils
| VC | 1 |  | 3.9 | 3 | 1.5 | 17.55
| Tank | 1 | 5 |  |  | 1.5 | 117.8097
| washout pipe trench | 1 |  | 4 | 0.6 | 0.9 | 2.16
[7 empty] | 137.5197 | m3 | 1089.74 | 149860.7446 | 2.14
3 | Back filling with loose soils | 1 |  |  |  | 1.1 | 24.4926 | m3 | 544.87 | 13345.3057 | 2.39a
4 | Boulder Soling with sand
| VC | 1 |  | 3.9 | 3 | 0.15 | 1.755
| Tank | 1 | 5 |  |  | 0.2 | 15.708
[7 empty] | 17.463 | m3 | 5141.87 | 89792.2869 | 6.5a
4 | RRM in 1:6 c/s mortar in VC
| vc | 1 |  | 9.05 | 0.45 | 1.5 | 6.1088
[7 empty] | 6.1088 | m3 | 14084.92 | 86041.2551 | 6.1c
1 | PCC(1:3:6) work as Lean Concrete for floor | 1 | 4.8 |  |  | 0.1 | 7.2382 | m3 | 14330.41 | 103726.796 | 7.2c
2 | PCC (1:2:4) in RCC components
| cover slab of VC | 2 |  | 3.9 | 3 | 0.1 | 2.34
[7 empty] | 2.34 | m3 | 15694.9 | 36726.066 | 7.2c
3 | PCC (1:1.5:3) for RCC components with 2 % WPC
| Base slab | 1 | 4.8 |  |  | 0.3 | 21.7147
| Circular wall | 1 | 4.5 |  |  | 3 | 16.9646
| Haunch at base | 0.5 |  | 25.7611 | 0.2 | 0.2 | 0.51522
| Circular dome beam | 1 |  | 28.2743 | 0.3 | 0.2 | 1.6965
| Conical roof slab | 1 | 4.5 |  |  |  | 13.3939
| Deduction for Manhole cover | 1 | 0.3 |  |  |  | -0.056549
[7 empty] | 54.2283 | m3 | 16966.81 | 920081.9524 | 7.4b1
4 | Formwork for concreting work
| bottom of cover slab of VC | 1 |  | 3.55 | 2.3 |  | 8.165
| sides of cover slab of VC | 1 |  | 9.9 |  | 0.1 | 0.99
| sides of base slab of tank | 1 | 4.8 | 30.1593 |  | 0.3 | 9.0478
| tank walls | 2 | 4.8 | 30.1593 |  | 3 | 180.9557
| soffit of conical roof slab | 1 | 4.3 |  |  |  | 61.4324
| deduction for MH cover | 1 | 0.3 |  |  |  | -0.28274
[7 empty] | 260.3082 | m2 | 1278.27 | 332744.1943 | 8.2a
5 | Scafolding work | [5 empty] | 1 | job | 25000 | 25000 | LS
6 | Reinforcement work in RCC components |  |  |  |  | kg/m
(1) | 12mm @ 170 c/c both ways on both faces of base slab" | 202.3529 |  | 6.4483 |  | 0.89 | 1161.3043 | 0.17
(2) | 12mm vertical bars 160 c/c b/s upto 1.0m height" | 337.5 |  | 1.5 |  | 0.89 | 450.5625 | 0.16
(3) | 12mm vertical bars @ 160 c/c b/s for walls-long" | 337.5 |  | 3.5 |  | 0.89 | 1051.3125 | 0.16
(4) | 12mm circular hoop bars @ 150 c/c upto 1m height" | 6 |  | 28.2743 |  | 0.89 | 150.9849 | 0.15
(5) | 12mm inclined bars @ 160 c/c for base haunch" | 180 |  | 0.9 |  | 0.89 | 144.18 | 0.16
(6) | 12mm circular hoop bars @ 170 c/c 1m to 3m height" | 11 |  | 28.2743 |  | 0.89 | 276.8057 | 0.17
(7) | 8mm @ 150 c/c stirrups for beam" | 194.7787 |  | 1 |  | 0.395 | 76.9376 | 0.15
(8) | 12mm bars 8 nos for circular beam" | 8 |  | 29.2168 |  | 0.89 | 208.0237 | 0.18
(9) | 12mm radial arc bars @ 150 c/c for conical roofslab" | 180 |  | 4.5476 |  | 0.89 | 728.5208 | 0.15
(10) | 12mm circular bars @ 160 c/c for conical roof slab" | 28 |  | 15.0796 |  | 0.89 | 375.7847 | 0.16
(11) | 6mm Spacer bars(seperators)" | 80 |  | 0.5 |  | 0.22 | 8.8 | 0.5
(12) | 8mm @ 150 c/c both ways for VC" | 22.6667 |  | 1.5 |  | 0.395 | 13.43 | 0.15
[7 empty] | 4646.6469 | Kg | 123.56 | 574139.6911 | 7.5
7 | 12.5mm inside plaster in 1:3 c/s mortar with 2% WPC
| inner face of tank wall | 1 | 4.3 |  |  | 3 | 81.0531
| floor | 1 | 4.3 |  |  |  | 58.088
[7 empty] | 139.1411 | m2 | 486.67 | 67715.8179 | 12.1a
8 | 12.5mm outside plaster in 1:4 c/m
| outer face of tank wall | 1 | 4.7 |  |  | 3 | 88.5929
| conical roof, both faces | 2 | 4.5 |  |  |  | 133.9392
| deduction for MH opening | 2 | 0.3 |  |  |  | -0.56549
[7 empty] | 221.9666 | m2 | 478.27 | 106159.9751 | 12.1c
9 | 3mm punning with 1:1 c/s mortar
| floor portion | 1 | 4.3 |  |  |  | 58.088
| inner face of wall | 1 | 4.3 |  |  | 3 | 81.0531
[7 empty] | 139.1411 | m2 | 332.33 | 46240.7746 | 11.20
10 | Double coat Snowcem paint on exposed surface
| outer face of wall | 1 | 4.7 |  |  | 1.5 | 44.2965
| conical roof | 1 | 4.7 |  |  | 1.72 | 72.7571
[7 empty] | 117.0536 | m2 | 200.01 | 23411.8908 | 13.4b
11 | 2 coats bitumen painting over unexposed surface
| floor portion | 1 | 4.3 |  |  |  | 58.088
| inner face of wall | 1 | 4.3 |  |  | 3 | 81.0531
[7 empty] | 139.1411 | m2 | 97.89 | 13620.5261 | 13.10b
12 | Supply and installation of outer and inner steel | 2 |  |  |  |  | 2 | set | 15000 | 30000 | LS
pipe ladders as directed by site Engineer
#REF! | 60 cm dia. MS MH cover including procuring | 2 |  |  |  |  | 2 | set | 3222 | 6444 | mh60
transporting and fixing at place,
#REF! | Installation of Pipe fittings | 1 |  |  |  |  | 1 | job | 15000 | 15000 | LS
#REF! | Construction site cleareance, leak proof test | 1 |  |  |  |  | 1 | job | 15000 | 15000 | LS
and disinfection of reservoir all complete
2687008.9972
B | Supply of Fittings for inlet, outlets,washout & overflow as per drawing, instruction and standard specification
2-1/2" Dia outlet -3 Nos
| 2-1/2" Dia 2m long G.I. Nipple | [5 empty] | 2 | pc | 3896 | 7792
| 2-1/2" Dia G.I. Nipple 30cm long | [5 empty] | 2 | pc | 1022 | 2044 |  | 4"
| 2-1/2" Dia G.I.Socket | [5 empty] | 1 | pc | 554 | 554
| 2-1/2" Dia G.I. Elbow | [5 empty] | 2 | pc | 805 | 1610
| 2-1/2" Dia G.I. Strainer50 cm long | [5 empty] | 2 | pc | 1774 | 3548
| 2-1/2" Dia Sluice valve | [5 empty] | 2 | pc | 11406 | 22812
| 2-1/2" Dia G.I. Flange | [5 empty] | 2 | set | 1699 | 3398
| 2-1/2" Dia G.I. /HDPE Flange | [5 empty] | 2 | set | 1824 | 3648
| 2-1/2" Dia C.I. Plug . | [5 empty] | 2 | pc | 214 | 428
| 2-1/2"*3/4" GI Unequal Tee | [5 empty] | 1 | pc | 1160 | 1160
| 3/4" GI nipple 2m long | [5 empty] | 2 | pc | 1271 | 2542
| 3/4" GI nipple 1 m long | [5 empty] | 1 | pc | 885.5 | 885.5
| 3/4" GI nipple 0.35 m long | [5 empty] | 1 | pc | 634.925 | 634.925
| 3/4"GI elbow | [5 empty] | 4 | pc | 94 | 376
| 3/4"GI Socket | [5 empty] | 2 | pc | 73 | 146
| 3/4"GIUnion | [5 empty] | 1 | pc | 238 | 238
| 3/4" short nipple 4" | [5 empty] | 3 | pc | 74 | 222
3" Dia overflow
| 3" Dia 2m long G.I. Nipple | [5 empty] | 2 | pc | 4645 | 9290
| 3" Dia G.I. Nipple 0.6 m long | [5 empty] | 1 | pc | 2093.5 | 2093.5
| 3" Dia G.I. Elbow | [5 empty] | 2 | pc | 1253 | 2506
| 3" Dia G.I. Socket | [5 empty] | 1 | pc | 817 | 817
| 3" Dia G.I. Plug . | [5 empty] | 1 | pc | 437 | 437
| 3" Dia G.I/HDPE.Flange Set. | [5 empty] | 1 | Set | 1950 | 1950
1-1/2" Dia Inlet - 1 No.
| 1-1/2" Dia 2m long G.I. Nipple | [5 empty] | 1 | pc | 2295 | 2295
| 1-1/2" Dia G.I. Nipple 1m long | [5 empty] | 1 | pc | 1447.5 | 1447.5
| 1-1/2" Dia G.I. Elbow | [5 empty] | 1 | pc | 308 | 308
| 1-1/2" Dia G.I. Socket | [5 empty] | 1 | pc | 208 | 208
| 1-1/2"Dia G.I. Short nipple | [5 empty] | 3 | pc | 116 | 348
| 1-1/2" Dia gate Valve | [5 empty] | 1 | pc | 3467 | 3467
| 1-1/2"Dia G.I. Plug . | [5 empty] | 1 | pc | 124 | 124
| 1-1/2" Dia G.I/HDPE.Flange Set. | [5 empty] | 2 | pc | 1332 | 2664
3" Dia Washout
| 3" Dia 2.8 m long G.I. Nipple | [5 empty] | 1 | Pc | 6103 | 6103
| 3" Dia Sluice valve | [5 empty] | 0 | pc | 13691 | 0
| 3" Dia G.I. Elbow | [5 empty] | 1 | pc | 1253 | 1253
| 3" Dia MS. Flange | [5 empty] | 2 | set | 1950 | 3900
| 3" Dia G.I. Plug . | [5 empty] | 1 | pc | 437 | 437
| 3" Dia G.I./HDPE Flange Set. | [5 empty] | 1 | set | 1950 | 1950
[9 empty] | Total | 93636.425 | Rs
2780645.4222

## reservoir 50 (hidden)
Shankharapur Municipaltiy Office
Office of Municipal Executuve
Bagmati Pradesh, Sankhu Kathmandu
Detail Measurement Sheet
Bill No: Final Bill
Contractor Name: SMO/079/80/84
Contractor's Name: Goldenstar Construction and Suppliers pvt. Ltd. ,Madhyapur thimi-3
Project: Construction of semi underground water tanks and sedimentaion tanks, Manichood Khanepani | [10 empty] | F/Y: 079/80
Location: Shankharapur-8 | [10 empty] | Date: 2080/3/21
S | DESCRIPTION | No | Rad. | L | B | H | QNTTY | Unit | Rate | Amount | norms
N |  |  | (m) | (m) | (m) | (m) |  |  | Rs | Rs | no.
| Wall Height = | 3 |  |  | 50 |  |  | Wall Thickness = |  | Wall Thickness = | 0.2
| Inside Dia. = | 5 |  | (Gross Volume = |  | 58.9049 | Cum) | Dome Height = |  | Dome Height = | 0.96
1 | Site Clearance | 1 | 5 |  |  |  | 78.5398 | job | 137.54 | 10802.3663 | LS
2 | Excavation work in BMS soils
| VC | 1 |  | 2.85 | 2.1 | 1.5 | 8.9775
| Tank | 1 | 3.2 |  |  | 1.5 | 48.2549
[7 empty] | 57.2324 | m3 | 1089.74 | 62368.3954 | 2.14
3 | Back filling with loose soils | 1 |  |  |  | 1.1 | 15.1621 | m3 | 544.87 | 8261.3797 | 2.39a
4 | Boulder Soling with sand
| VC | 1 |  | 2.85 | 2.1 | 0.15 | 0.89775
| Tank | 1 | 3.2 |  |  | 0.2 | 6.434
[7 empty] | 7.3317 | m3 | 5141.87 | 37698.8116 | 6.5a
4 | RRM in 1:6 c/s mortar in VC
| vc | 1 |  | 7.05 | 0.45 | 1 | 3.1725
[7 empty] | 3.1725 | m3 | 14084.92 | 44684.4087 | 6.1c
1 | PCC(1:3:6) work as Lean Concrete for floor | 1 | 3 |  |  | 0.1 | 2.8274 | m3 | 14330.41 | 40518.2797 | 7.2c
2 | PCC (1:2:4) in RCC components
| cover slab of VC | 2 |  | 2.85 | 2.1 | 0.08 | 0.9576
| manhole cover | -1 |  | 0.6 | 0.6 | 0.08 | -0.0288
[7 empty] | 0.9288 | m3 | 15694.9 | 14577.4231 | 7.2c
3 | PCC (1:1.5:3) for RCC components with 2 % WPC
| Base slab | 1 | 3 |  |  | 0.23 | 6.5031
| Circular wall | 1 | 2.7 |  |  | 3 | 10.1788
| Haunch at base | 0.5 |  | 14.4513 | 0.2 | 0.2 | 0.28903
| Circular dome beam | 1 |  | 16.9646 | 0.3 | 0.2 | 1.0179
| Conical roof slab | 1 | 2.7 |  |  |  | 4.8614
| Deduction for Manhole cover | 1 | 0.3 |  |  |  | -0.056549
[7 empty] | 22.7936 | m3 | 16966.81 | 386734.1372 | 7.4b1
4 | Formwork for concreting work
| bottom of cover slab of VC | 1 |  | 2.15 | 1.75 |  | 3.7625
| sides of cover slab of VC | 1 |  | 7.05 |  | 0.08 | 0.564
| sides of base slab of tank | 1 | 3 | 18.8496 |  | 0.23 | 4.3354
| tank walls | 2 | 3 | 18.8496 |  | 3 | 113.0973
| soffit of conical roof slab | 1 | 2.5 |  |  |  | 21.0328
| deduction for MH cover | 1 | 0.3 |  |  |  | -0.28274
[7 empty] | 142.5093 | m2 | 1278.27 | 182165.4009 | 8.2a
5 | Scafolding work | [5 empty] | 1 | job | 25000 | 25000 | LS
6 | Reinforcement work in RCC components |  |  |  |  | kg/m
(1) | 12mm @ 170 c/c both ways on both faces of base slab" | 117.6471 |  | 3.7471 |  | 0.89 | 392.3441 | 0.17
(2) | 12mm vertical bars 160 c/c b/s upto 1.0m height" | 200 |  | 1.5 |  | 0.89 | 267 | 0.16
(3) | 12mm vertical bars @ 160 c/c b/s for walls-long" | 200 |  | 3.5 |  | 0.89 | 623 | 0.16
(4) | 12mm circular hoop bars @ 150 c/c upto 1m height" | 6 |  | 16.9646 |  | 0.89 | 90.591 | 0.15
(5) | 12mm inclined bars @ 160 c/c for base haunch" | 104 |  | 0.9 |  | 0.89 | 83.304 | 0.16
(6) | 12mm circular hoop bars @ 170 c/c 1m to 3m height" | 11 |  | 16.9646 |  | 0.89 | 166.0834 | 0.17
(7) | 8mm @ 150 c/c stirrups for beam" | 119.3805 |  | 1 |  | 0.395 | 47.1553 | 0.15
(8) | 12mm bars 8 nos for circular beam" | 8 |  | 17.9071 |  | 0.89 | 127.4984 | 0.18
(9) | 12mm radial arc bars @ 150 c/c for conical roofslab" | 104 |  | 2.678 |  | 0.89 | 247.8742 | 0.15
(10) | 12mm circular bars @ 160 c/c for conical roof slab" | 16 |  | 9.4248 |  | 0.89 | 134.2088 | 0.16
(11) | 6mm Spacer bars(seperators)" | 44 |  | 0.5 |  | 0.22 | 4.84 | 0.5
(12) | 8mm @ 150 c/c both ways for VC" | 22.6667 |  | 1.5 |  | 0.395 | 13.43 | 0.15
[7 empty] | 2197.3293 | Kg | 123.56 | 271502.0058 | 7.5
7 | 12.5mm inside plaster in 1:3 c/s mortar with 2% WPC
| inner face of tank wall | 1 | 2.5 |  |  | 3 | 47.1239
| floor | 1 | 2.5 |  |  |  | 19.635
[7 empty] | 66.7588 | m2 | 486.67 | 32489.5266 | 12.1a
8 | 12.5mm outside plaster in 1:4 c/m
| outer face of tank wall | 1 | 2.9 |  |  | 3 | 54.6637
| conical roof, both faces | 2 | 2.7 |  |  |  | 48.6136
| deduction for MH opening | 2 | 0.3 |  |  |  | -0.56549
[7 empty] | 102.7118 | m2 | 478.27 | 49123.971 | 12.1c
9 | 3mm punning with 1:1 c/s mortar
| floor portion | 1 | 2.5 |  |  |  | 19.635
| inner face of wall | 1 | 2.5 |  |  | 3 | 47.1239
[7 empty] | 66.7588 | m2 | 332.33 | 22185.9666 | 11.20
10 | Double coat Snowcem paint on exposed surface
| outer face of wall | 1 | 2.9 |  |  | 1.5 | 27.3319
| conical roof | 1 | 2.9 |  |  | 1 | 27.8308
[7 empty] | 55.1627 | m2 | 200.01 | 11033.0859 | 13.4b
11 | 2 coats bitumen painting over unexposed surface
| floor portion | 1 | 2.5 |  |  |  | 19.635
[7 empty] | 19.635 | m2 | 97.89 | 1922.0657 | 13.10b |  | 33706.1122
12 | Supply and installation of outer and inner steel | 2 |  |  |  |  | 2 | set | 15000 | 30000 | LS
pipe ladders as directed by site Engineer
#REF! | 60 cm dia. MS MH cover including procuring | 2 |  |  |  |  | 2 | set | 3222 | 6444 | mh60
transporting and fixing at place,
#REF! | Installation of Pipe fittings | 1 |  |  |  |  | 1 | job | 15000 | 15000 | LS
#REF! | Construction site cleareance, leak proof test | 1 |  |  |  |  | 1 | job | 15000 | 15000 | LS
and disinfection of reservoir all complete
1267511.2241
B | Supply of Fittings for inlet, outlets,washout & overflow as per drawing, instruction and standard specification
2-1/2" Dia outlet -3 Nos
| 2-1/2" Dia 2m long G.I. Nipple | [5 empty] | 2 | pc | 3896 | 7792
| 2-1/2" Dia G.I. Nipple 30cm long | [5 empty] | 2 | pc | 1022 | 2044 |  | 4"
| 2-1/2" Dia G.I.Socket | [5 empty] | 1 | pc | 554 | 554
| 2-1/2" Dia G.I. Elbow | [5 empty] | 2 | pc | 805 | 1610
| 2-1/2" Dia G.I. Strainer50 cm long | [5 empty] | 2 | pc | 1774 | 3548
| 2-1/2" Dia Sluice valve | [5 empty] | 2 | pc | 11406 | 22812
| 2-1/2" Dia G.I. Flange | [5 empty] | 2 | set | 1699 | 3398
| 2-1/2" Dia G.I. /HDPE Flange | [5 empty] | 2 | set | 1824 | 3648
| 2-1/2" Dia C.I. Plug . | [5 empty] | 2 | pc | 214 | 428
| 2-1/2"*3/4" GI Unequal Tee | [5 empty] | 1 | pc | 1160 | 1160
| 3/4" GI nipple 2m long | [5 empty] | 2 | pc | 1271 | 2542
| 3/4" GI nipple 1 m long | [5 empty] | 1 | pc | 885.5 | 885.5
| 3/4" GI nipple 0.35 m long | [5 empty] | 1 | pc | 634.925 | 634.925
| 3/4"GI elbow | [5 empty] | 4 | pc | 94 | 376
| 3/4"GI Socket | [5 empty] | 2 | pc | 73 | 146
| 3/4"GIUnion | [5 empty] | 1 | pc | 238 | 238
| 3/4" short nipple 4" | [5 empty] | 3 | pc | 74 | 222
3" Dia overflow
| 3" Dia 2m long G.I. Nipple | [5 empty] | 2 | pc | 4645 | 9290
| 3" Dia G.I. Nipple 0.6 m long | [5 empty] | 1 | pc | 2093.5 | 2093.5
| 3" Dia G.I. Elbow | [5 empty] | 2 | pc | 1253 | 2506
| 3" Dia G.I. Socket | [5 empty] | 1 | pc | 817 | 817
| 3" Dia G.I. Plug . | [5 empty] | 1 | pc | 437 | 437
| 3" Dia G.I/HDPE.Flange Set. | [5 empty] | 1 | Set | 1950 | 1950
1-1/2" Dia Inlet - 1 No.
| 1-1/2" Dia 2m long G.I. Nipple | [5 empty] | 1 | pc | 2295 | 2295
| 1-1/2" Dia G.I. Nipple 1m long | [5 empty] | 1 | pc | 1447.5 | 1447.5
| 1-1/2" Dia G.I. Elbow | [5 empty] | 1 | pc | 308 | 308
| 1-1/2" Dia G.I. Socket | [5 empty] | 1 | pc | 208 | 208
| 1-1/2"Dia G.I. Short nipple | [5 empty] | 3 | pc | 116 | 348
| 1-1/2" Dia gate Valve | [5 empty] | 1 | pc | 3467 | 3467
| 1-1/2"Dia G.I. Plug . | [5 empty] | 1 | pc | 124 | 124
| 1-1/2" Dia G.I/HDPE.Flange Set. | [5 empty] | 2 | pc | 1332 | 2664
3" Dia Washout
| 3" Dia 2.8 m long G.I. Nipple | [5 empty] | 1 | Pc | 6103 | 6103
| 3" Dia Sluice valve | [5 empty] | 0 | pc | 13691 | 0
| 3" Dia G.I. Elbow | [5 empty] | 1 | pc | 1253 | 1253
| 3" Dia MS. Flange | [5 empty] | 2 | set | 1950 | 3900
| 3" Dia G.I. Plug . | [5 empty] | 1 | pc | 437 | 437
| 3" Dia G.I./HDPE Flange Set. | [5 empty] | 1 | set | 1950 | 1950
[9 empty] | Total | 93636.425 | Rs
1361147.6491
#REF!

## wcr (hidden)
Shankharapur Municipaltiy Office
Office of Municipal Executuve
Bagmati Pradesh, Sankhu Kathmandu
Work Completion Report
Bill No: Final Bill
Contractor Name: SMO/079/80/84
Contractor's Name: Goldenstar Construction and Suppliers pvt. Ltd. ,Madhyapur thimi-3
Project: Construction of semi underground water tanks and sedimentaion tanks, Manichood Khanepani | [8 empty] | F/Y: 079/80
Location: Shankharapur-8 | [8 empty] | Date: 2080/3/21
S.No. | Description of Works | Unit | Quantity | Rate | Amount | Quantity | Amount |  | Remarks
Reservoir 50,150,200, 3 sedimentation tank, barbed wire fencing
1 | Site Clearance-off rooting of small trees, bushes and removing of top soil for 3 semi underground reservoirs and 3 sedimentation tanks | m2 | 870.8 | 80 | 69664 | 909.2526 | 72740.2079 | 3076.2079 |  | 4.4158
2 | Excavation work in Soft soils for semi underground water tanks and sedimentation tanks all complete as per specifications | m3 | 827.1 | 80 | 66168 | 758.3624 | 60668.9951 | -5499.0049 |  | -8.3107
3 | Earth work in refilling with ordinary hard soil in 15cm layers including water sprinking and compaction after each layer all complete | m3 | 165.8 | 100 | 16580 | 97.2718 | 9727.1841 | -6852.8159 |  | -41.3318
4 | Boulder Soling with sand for the foundation of structures as per required specification all complete | m3 | 101.26 | 3200 | 324032 | 85.5087 | 273627.9738 | -50404.0262 |  | -15.5553
5 | Stone masonry in 1:6 c/s mortar in valve chamber and boundary wall as per required specification all complete | m3 | 134.55 | 6000 | 807300 | 75.1012 | 450607.5 | -356692.5 |  | -44.1834
6 | Providing and laying PCC(1:3:6) work as Lean Concrete for floor as per required specification for foundation of water tank and sedimentation tank all complete | m3 | 42.8 | 6600 | 282480 | 35.5226 | 234448.8536 | -48031.1464 |  | -17.0034
7 | Providing and laying of PCC (1:2:4) in RCC components in Valve chamber and in RRM works all complete | m3 | 13.98 | 8000 | 111840 | 6.8603 | 54882.4 | -56957.6 |  | -50.9278
8 | Providing and laying of PCC (1:1.5:3) for RCC components with 2 % WPC in structutral components of water tank and sedimentation tank al complete | m3 | 206.51 | 12800 | 2643328 | 237.281 | 3037196.2296 | 393868.2296 |  | 14.9005
9 | Providing of Formwork for concreting work in water tank and sedimentaion tank as per drawing and specification all complete | m2 | 1260.37 | 250 | 315092.5 | 1387.6408 | 346910.1882 | 31817.6882 |  | 10.0979
10 | Providing of extra Scafolding work(support for top slab) in water tank | ls | 3 | 10000 | 30000 | 3 | 30000 | 0 |  | 0
11 | Cutting bending,placing in position and binding Reinforcement steel bar in bottom slab wall ring beam, spherical dome of the tank and valve chamber cover slab and bottom as well as walls of sedimentation tank according to the drawing and specification (Size and quantity of bars required are given in Drg | kg | 27572.68 | 110 | 3032994.8 | 27234.3429 | 2995777.7141 | -37217.0859 |  | -1.2271
12 | Brick Masonry Work in 1:6 cement sand mortar for sedimentation tank all complete | m3 | 7.86 | 11500 | 90390 | 0 | 0 | -90390 |  | -100
13 | Providing 12.5mm inside plaster in 1:3 c/s mortar with 2% WPC for water tank and sedimentation tank | m2 | 1178.83 | 280 | 330072.4 | 1162.9948 | 325638.5436 | -4433.8564 |  | -1.3433
14 | Providing 12.5mm outside plaster in 1:4 c/m for water tank and sedimentation tank | m2 | 600.55 | 280 | 168154 | 626.21 | 175338.7891 | 7184.7891 |  | 4.2727
15 | Providing 3mm punning with 1:1 c/s mortar for water tank and sedimentation tank | m2 | 894.58 | 100 | 89458 | 850.9948 | 85099.4799 | -4358.5201 |  | -4.8721
16 | Providing Double coat Snowcem paint on exposed surface of structures | m2 | 317.04 | 120 | 38044.8 | 330.2463 | 39629.556 | 1584.756 |  | 4.1655
17 | Providing 2 coats bitumen painting over unexposed surface on water tank | m2 | 376.18 | 120 | 45141.6 | 344.3264 | 41319.1691 | -3822.4309 |  | -8.4676
18 | Providing Two Coat of Enamel Paint of Appropriate Colour on Exposed Surface of sedimentation Tank | m2 | 206.67 | 120 | 24800.4 | 312 | 37440 | 12639.6 |  | 50.9653
19 | Supply and installation of outer and inner steel pipe ladders as directed by site Engineer | ls | 6 | 20000 | 120000 | 6 | 120000 | 0 |  | 0
20 | 60 cm dia. MS MH cover including procuring transporting and fixing at place, | nos | 12 | 10000 | 120000 | 10 | 100000 | -20000 |  | -16.6667
21 | Installation of Pipe fittings for water tanks | ls | 3 | 20000 | 60000 | 3 | 60000 | 0 |  | 0
22 | Construction site cleareance, leak proof test and disinfection of reservoir all complete | ls | 3 | 20000 | 60000 | 3 | 60000 | 0 |  | 0
23 | Supply of Fittings for outlet of water tanks , 2-1/2" Dia 2m long G.I. Nipple | pc | 6 | 5500 | 33000 | 6 | 33000 | 0 |  | 0
24 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Nipple 30cm long | pc | 6 | 1600 | 9600 | 6 | 9600 | 0 |  | 0
25 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I.Socket | pc | 3 | 500 | 1500 | 3 | 1500 | 0 |  | 0
26 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Elbow | pc | 6 | 780 | 4680 | 6 | 4680 | 0 |  | 0
27 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Strainer50 cm long | pc | 6 | 2200 | 13200 | 6 | 13200 | 0 |  | 0
28 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia Sluice valve | pc | 6 | 80 | 480 | 6 | 480 | 0 |  | 0
29 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Flange | set | 6 | 610 | 3660 | 6 | 3660 | 0 |  | 0
30 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. /HDPE Flange | set | 6 | 1600 | 9600 | 6 | 9600 | 0 |  | 0
31 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia C.I. Plug . | pc | 6 | 230 | 1380 | 6 | 1380 | 0 |  | 0
32 | Supply of Fittings for outlet of water tanks ,2-1/2"*3/4" GI Unequal Tee | pc | 3 | 1100 | 3300 | 3 | 3300 | 0 |  | 0
33 | Supply of Fittings for outlet of water tanks ,3/4" GI nipple 2m long | pc | 6 | 1500 | 9000 | 6 | 9000 | 0 |  | 0
34 | Supply of Fittings for outlet of water tanks ,3/4" GI nipple 1 m long | pc | 3 | 780 | 2340 | 3 | 2340 | 0 |  | 0
35 | Supply of Fittings for outlet of water tanks ,3/4" GI nipple 0.35 m long | pc | 3 | 350 | 1050 | 3 | 1050 | 0 |  | 0
36 | Supply of Fittings for outlet of water tanks ,3/4"GI elbow | pc | 12 | 110 | 1320 | 12 | 1320 | 0 |  | 0
37 | Supply of Fittings for outlet of water tanks ,3/4"GI Socket | pc | 6 | 100 | 600 | 6 | 600 | 0 |  | 0
38 | Supply of Fittings for outlet of water tanks ,3/4"GIUnion | pc | 3 | 210 | 630 | 3 | 630 | 0 |  | 0
39 | Supply of Fittings for outlet of water tanks ,3/4" short nipple 4" | pc | 9 | 100 | 900 | 9 | 900 | 0 |  | 0
40 | Supply of Fittings for overflow of water tanks ,3" Dia 2m long G.I. Nipple | pc | 6 | 6900 | 41400 | 6 | 41400 | 0 |  | 0
41 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Nipple 0.6 m long | pc | 3 | 1710 | 5130 | 3 | 5130 | 0 |  | 0
42 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Elbow | pc | 6 | 1270 | 7620 | 6 | 7620 | 0 |  | 0
43 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Socket | pc | 3 | 880 | 2640 | 3 | 2640 | 0 |  | 0
44 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Plug . | pc | 3 | 460 | 1380 | 3 | 1380 | 0 |  | 0
45 | Supply of Fittings for overflow of water tanks ,3" Dia G.I/HDPE.Flange Set. | Set | 3 | 1900 | 5700 | 3 | 5700 | 0 |  | 0
46 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia 2m long G.I. Nipple | pc | 3 | 3000 | 9000 | 3 | 9000 | 0 |  | 0
47 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I. Nipple 1m long | pc | 3 | 1500 | 4500 | 3 | 4500 | 0 |  | 0
48 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I. Elbow | pc | 3 | 350 | 1050 | 3 | 1050 | 0 |  | 0
49 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I. Socket | pc | 3 | 300 | 900 | 3 | 900 | 0 |  | 0
50 | Supply of Fittings for inlet of water tanks ,1-1/2"Dia G.I. Short nipple | pc | 9 | 230 | 2070 | 9 | 2070 | 0 |  | 0
51 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia gate Valve | pc | 3 | 3500 | 10500 | 3 | 10500 | 0 |  | 0
52 | Supply of Fittings for inlet of water tanks ,1-1/2"Dia G.I. Plug . | pc | 3 | 80 | 240 | 3 | 240 | 0 |  | 0
53 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I/HDPE.Flange Set. | pc | 6 | 1110 | 6660 | 6 | 6660 | 0 |  | 0
54 | Supply of Fittings for washout of water tanks ,3" Dia 2.8 m long G.I. Nipple | Pc | 3 | 9000 | 27000 | 3 | 27000 | 0 |  | 0
55 | Supply of Fittings for washout of water tanks ,3" Dia G.I. Elbow | pc | 3 | 1100 | 3300 | 3 | 3300 | 0 |  | 0
56 | Supply of Fittings for washout of water tanks ,3" Dia MS. Flange | set | 6 | 700 | 4200 | 6 | 4200 | 0 |  | 0
57 | Supply of Fittings for washout of water tanks ,3" Dia G.I. Plug . | pc | 3 | 400 | 1200 | 3 | 1200 | 0 |  | 0
58 | Supply of Fittings for washout of water tanks ,3" Dia G.I./HDPE Flange Set. | set | 3 | 1850 | 5550 | 3 | 5550 | 0 |  | 0
59 | Providing and fixing of Barbed wire fencing all complete | rm | 1724.58 | 1000 | 1724580 | 1782.96 | 1782960 | 58380 |  | 3.3852
60 | providing 6 mm ø mild steel rod for hooks, 650 mm long each for fencing works | kg | 35.4 | 150 | 5310 | 0 | 0 | -5310 |  | -100
61 | providing M.S. 40 x 40 x 6 angle bar, 2.5 m long for fencing all complete | kg | 1077.99 | 150 | 161698.5 | 560 | 84000 | -77698.5 |  | -48.0515
62 | Providing and laying granular sub-base without compaction on prepared surface, mixing , complete as per Drawing and Technical Specifications., By Mechanical means | m3 | 135 | 2500 | 337500 |  | 0 | -337500 |  | -100
63 | Earthwork Excavation in Cutting., Roadway Excavation in all types of Soil by Mechanical Means ., Road way Excavation in all types of soil as per Drawing and technical specifications including removal of stumps and other deleterious matter, all lifts and lead as per Drawing and instruction of the Engineer as required on site for Access road required for the proposed Structures | m3 | 600 | 50 | 30000 | 440 | 22000 | -8000 |  | -26.6667
| Total |  |  |  | 11340909 |  | 10736292.7841 | -604616.2159 |  | 94.6687 | #REF! | #REF!
| VAT 13% |  |  |  | 1474318.17 |  | 1395718.0619 | -78600.1081
| All Total |  |  |  | 12815227.17 |  | 12132010.846 | -683216.324
| Project information Board with metal frame on site | ps | 3 | 5000 | 15000 | 2 | 5000 | -10000
| Lab test for concrete as instructed by site engineer | ps | 1 | 45000 | 45000 | 1 | 45000 | 0
| Insurance | ps | 1 | 30000 | 30000 | 1 | 30000 | 0
| Supply of required fittings and required materials and extra works on site as per the approval of Engineer | ps | 1 | 300000 | 300000 | 1 | 235113.02 | -64886.98
| Total |  |  |  | 13205227.17 |  | 12447123.866 | -758103.304

## Sheet1 (hidden)
Shankharapur Municipaltiy Office
Office of Municipal Executuve
Bagmati Pradesh, Sankhu Kathmandu
Abstract of Cost
Bill No: Final Bill
Contractor Name: SMO/079/80/84
Contractor's Name: Goldenstar Construction and Suppliers pvt. Ltd. ,Madhyapur thimi-3
Project: Construction of semi underground water tanks and sedimentaion tanks, Manichood Khanepani | [5 empty] | F/Y: 079/80
Location: Shankharapur-8 | [5 empty] | Date: 2080/3/21
S.No. | Description of Works | Unit | Quantity | Rate | Amount | Remarks
Reservoir 50,150,200, 3 sedimentation tank, barbed wire fencing
1 | Site Clearance-off rooting of small trees, bushes and removing of top soil for 3 semi underground reservoirs and 3 sedimentation tanks | m2 | 909.2526 | 80 | 72740.2079
2 | Excavation work in Soft soils for semi underground water tanks and sedimentation tanks all complete as per specifications | m3 | 758.3624 | 80 | 60668.9951
3 | Earth work in refilling with ordinary hard soil in 15cm layers including water sprinking and compaction after each layer all complete | m3 | 97.2718 | 100 | 9727.1841
4 | Boulder Soling with sand for the foundation of structures as per required specification all complete | m3 | 85.5087 | 3200 | 273627.9738
5 | Stone masonry in 1:6 c/s mortar in valve chamber and boundary wall as per required specification all complete | m3 | 75.1012 | 6000 | 450607.5
6 | Providing and laying PCC(1:3:6) work as Lean Concrete for floor as per required specification for foundation of water tank and sedimentation tank all complete | m3 | 35.5226 | 6600 | 234448.8536
7 | Providing and laying of PCC (1:2:4) in RCC components in Valve chamber and in RRM works all complete | m3 | 6.8603 | 8000 | 54882.4
8 | Providing and laying of PCC (1:1.5:3) for RCC components with 2 % WPC in structutral components of water tank and sedimentation tank al complete | m3 | 237.281 | 12800 | 3037196.2296
9 | Providing of Formwork for concreting work in water tank and sedimentaion tank as per drawing and specification all complete | m2 | 1387.6408 | 250 | 346910.1882
10 | Providing of extra Scafolding work(support for top slab) in water tank | ls | 3 | 10000 | 30000
11 | Cutting bending,placing in position and binding Reinforcement steel bar in bottom slab wall ring beam, spherical dome of the tank and valve chamber cover slab and bottom as well as walls of sedimentation tank according to the drawing and specification (Size and quantity of bars required are given in Drg | kg | 27234.3429 | 110 | 2995777.7141
12 | Brick Masonry Work in 1:6 cement sand mortar for sedimentation tank all complete | m3 | 0 | 11500 | 0
13 | Providing 12.5mm inside plaster in 1:3 c/s mortar with 2% WPC for water tank and sedimentation tank | m2 | 1162.9948 | 280 | 325638.5436
14 | Providing 12.5mm outside plaster in 1:4 c/m for water tank and sedimentation tank | m2 | 626.21 | 280 | 175338.7891
15 | Providing 3mm punning with 1:1 c/s mortar for water tank and sedimentation tank | m2 | 850.9948 | 100 | 85099.4799
16 | Providing Double coat Snowcem paint on exposed surface of structures | m2 | 330.2463 | 120 | 39629.556
17 | Providing 2 coats bitumen painting over unexposed surface on water tank | m2 | 344.3264 | 120 | 41319.1691
18 | Providing Two Coat of Enamel Paint of Appropriate Colour on Exposed Surface of sedimentation Tank | m2 | 312 | 120 | 37440
19 | Supply and installation of outer and inner steel pipe ladders as directed by site Engineer | ls | 6 | 20000 | 120000
20 | 60 cm dia. MS MH cover including procuring transporting and fixing at place, | nos | 10 | 10000 | 100000
21 | Installation of Pipe fittings for water tanks | ls | 3 | 20000 | 60000
22 | Construction site cleareance, leak proof test and disinfection of reservoir all complete | ls | 3 | 20000 | 60000
23 | Supply of Fittings for outlet of water tanks , 2-1/2" Dia 2m long G.I. Nipple | pc | 6 | 5500 | 33000 |  | 3
24 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Nipple 30cm long | pc | 6 | 1600 | 9600 |  | 3
25 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I.Socket | pc | 3 | 500 | 1500 |  | 3
26 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Elbow | pc | 6 | 780 | 4680 |  | 3
27 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Strainer50 cm long | pc | 6 | 2200 | 13200 |  | 3
28 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia Sluice valve | pc | 6 | 80 | 480 |  | 3
29 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Flange | set | 6 | 610 | 3660 |  | 3
30 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. /HDPE Flange | set | 6 | 1600 | 9600 |  | 3
31 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia C.I. Plug . | pc | 6 | 230 | 1380 |  | 3
32 | Supply of Fittings for outlet of water tanks ,2-1/2"*3/4" GI Unequal Tee | pc | 3 | 1100 | 3300 |  | 3
33 | Supply of Fittings for outlet of water tanks ,3/4" GI nipple 2m long | pc | 6 | 1500 | 9000 |  | 3
34 | Supply of Fittings for outlet of water tanks ,3/4" GI nipple 1 m long | pc | 3 | 780 | 2340 |  | 3
35 | Supply of Fittings for outlet of water tanks ,3/4" GI nipple 0.35 m long | pc | 3 | 350 | 1050 |  | 3
36 | Supply of Fittings for outlet of water tanks ,3/4"GI elbow | pc | 12 | 110 | 1320 |  | 3
37 | Supply of Fittings for outlet of water tanks ,3/4"GI Socket | pc | 6 | 100 | 600 |  | 3
38 | Supply of Fittings for outlet of water tanks ,3/4"GIUnion | pc | 3 | 210 | 630 |  | 3
39 | Supply of Fittings for outlet of water tanks ,3/4" short nipple 4" | pc | 9 | 100 | 900 |  | 3
40 | Supply of Fittings for overflow of water tanks ,3" Dia 2m long G.I. Nipple | pc | 6 | 6900 | 41400 |  | 3
41 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Nipple 0.6 m long | pc | 3 | 1710 | 5130 |  | 3
42 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Elbow | pc | 6 | 1270 | 7620 |  | 3
43 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Socket | pc | 3 | 880 | 2640 |  | 3
44 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Plug . | pc | 3 | 460 | 1380 |  | 3
45 | Supply of Fittings for overflow of water tanks ,3" Dia G.I/HDPE.Flange Set. | Set | 3 | 1900 | 5700 |  | 3
46 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia 2m long G.I. Nipple | pc | 3 | 3000 | 9000 |  | 3
47 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I. Nipple 1m long | pc | 3 | 1500 | 4500 |  | 3
48 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I. Elbow | pc | 3 | 350 | 1050 |  | 3
49 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I. Socket | pc | 3 | 300 | 900 |  | 3
50 | Supply of Fittings for inlet of water tanks ,1-1/2"Dia G.I. Short nipple | pc | 9 | 230 | 2070 |  | 3
51 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia gate Valve | pc | 3 | 3500 | 10500 |  | 3
52 | Supply of Fittings for inlet of water tanks ,1-1/2"Dia G.I. Plug . | pc | 3 | 80 | 240 |  | 3
53 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I/HDPE.Flange Set. | pc | 6 | 1110 | 6660 |  | 3
54 | Supply of Fittings for washout of water tanks ,3" Dia 2.8 m long G.I. Nipple | Pc | 3 | 9000 | 27000 |  | 3
55 | Supply of Fittings for washout of water tanks ,3" Dia G.I. Elbow | pc | 3 | 1100 | 3300 |  | 3
56 | Supply of Fittings for washout of water tanks ,3" Dia MS. Flange | set | 6 | 700 | 4200 |  | 3
57 | Supply of Fittings for washout of water tanks ,3" Dia G.I. Plug . | pc | 3 | 400 | 1200 |  | 3
58 | Supply of Fittings for washout of water tanks ,3" Dia G.I./HDPE Flange Set. | set | 3 | 1850 | 5550 |  | 3
59 | Providing and fixing of Barbed wire fencing all complete | rm | 1782.96 | 1000 | 1782960
60 | providing 6 mm ø mild steel rod for hooks, 650 mm long each for fencing works | kg | 0 | 150 | 0
61 | providing M.S. 40 x 40 x 6 angle bar, 2.5 m long for fencing all complete | kg | 560 | 150 | 84000
62 | Providing and laying granular sub-base without compaction on prepared surface, mixing , complete as per Drawing and Technical Specifications., By Mechanical means | m3 | 0 | 2500 | 0
63 | Earthwork Excavation in Cutting., Roadway Excavation in all types of Soil by Mechanical Means ., Road way Excavation in all types of soil as per Drawing and technical specifications including removal of stumps and other deleterious matter, all lifts and lead as per Drawing and instruction of the Engineer as required on site for Access road required for the proposed Structures | m3 | 440 | 50 | 22000
|  |  |  | Total | 10736292.7841 |  |  | #REF! | #REF!
|  |  |  | VAT | 1395718.0619
|  |  |  | All Total | 12132010.846
| Project information Board with metal frame on site | ps | 2 | 5000 | 10000
| Lab test for concrete as instructed by site engineer | ps | 1 | 45000 | 45000
| Insurance | ps | 1 | 30000 | 30000
| Supply of required fittings and required materials and extra works on site as per the approval of Engineer | ps | 1 | 235113.02 | 235113.02
|  |  |  | Grand Total | 12452123.866

## st quantity (hidden)
Shankharapur Municipaltiy Office
Office of Municipal Executuve
Bagmati Pradesh, Sankhu Kathmandu
Detail Measurement Sheet
Bill No: Final Bill
Contractor Name: SMO/079/80/84
Contractor's Name: Goldenstar Construction and Suppliers pvt. Ltd. ,Madhyapur thimi-3
Project: Construction of semi underground water tanks and sedimentaion tanks, Manichood Khanepani | [6 empty] | F/Y: 079/80
Location: Shankharapur-8 | [6 empty] | Date: 2080/3/21
Detail Measurement Sheet
Component: Plain Sedimentation Tank
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units
1 | Site Clearence | 3 | 14 | 6 |  | 252 | m2
2 | Earth Work in Excavation in Boulder Mixed Soil
| Dham | 1 | 14.5 | 6.5 | 1.5 | 141.38
| Ranatole | 1 | 14.5 | 6.5 | 1.5 | 141.38
| goldhunga | 1 | 12.5 | 6 | 1 | 75
|  |  |  | Total |  | 357.76 | m3
3 | Earth Filling in Foundation
| Dham | 1 | 14.5 | 0.8 | 2 | 23.2
|  | 1 | 5 | 0.5 | 2 | 5 | both side
|  |  |  | Sub Total |  | 28.2 | m3
4 | Stone Soling with sand packing on
| Base of Foundation, dham | 1 | 12.4 | 4.4 | 0.2 | 10.91
| chamber | 1 | 1 | 1 | 0.15 | 0.15
| Base of Foundation, ranatole | 1 | 12.3 | 4.4 | 0.2 | 10.82
| chamber | 1 | 1 | 1 | 0.15 | 0.15
| Base of Foundation, goldhunga | 1 | 10.5 | 4 | 0.2 | 8.4
| chamber | 1 | 1 | 1 | 0.15 | 0.15
|  |  |  | Total |  | 30.58 | m3
5 | Laying of P.C.C. 1:3:6 on Base of
| Base of Foundation, dham | 1 | 12.4 | 4.4 | 0.1 | 5.46
| Base of Foundation, ranatole | 1 | 12.3 | 4.4 | 0.1 | 5.41
| Base of Foundation, goldhunga | 1 | 10.5 | 4 | 0.1 | 4.2
|  |  |  | Total |  | 15.07 | m3
6 | Laying of One Layer Tarfelt Over
|  |  |  | Total |  | 0 | m3
7 | P.C.C (1: 1.5:3) Works for R.C.C
Dham
| Base Slab | 1 | 12.4 | 4.4 | 0.18 | 9.82
| long wall | 2 | 12.25 | 0.15 | 2.8 | 10.29
| shortwall | 2 | 4.25 | 0.15 | 2.8 | 3.57
| outlet dedn | -1 | 3.7 | 0.15 | 0.2 | -0.11
| inlet | 1 | 4 | 0.55 | 0.075 | 0.17
| outlet | 1 | 3.7 | 0.55 | 0.075 | 0.15
| medium wall | 1 | 4 | 0.15 | 2 | 1.2
| baffle wall | 1 | 4 | 0.15 | 0.9 | 0.54
| top | 2 | 13.3 | 0.45 | 0.333 | 3.99
|  | 1 | 4.4 | 0.45 | 0.333 | 0.66
| chamber | 4 | 0.9 | 0.1 | 0.9 | 0.32
| cover | 1 | 1 | 1 | 0.1 | 0.1
| less | -1 | 0.6 | 0.6 | 0.1 | -0.04
Ranatole
| Base Slab | 1 | 12.3 | 4.4 | 0.18 | 9.74
| long wall | 2 | 12.15 | 0.15 | 2.8 | 10.21
| shortwall | 2 | 4.25 | 0.15 | 2.8 | 3.57
| outlet dedn | -1 | 3.7 | 0.15 | 0.2 | -0.11
| inlet | 1 | 4 | 0.55 | 0.075 | 0.17
| outlet | 1 | 3.7 | 0.55 | 0.075 | 0.15
| medium wall | 1 | 4 | 0.15 | 2 | 1.2
| baffle wall | 1 | 4 | 0.15 | 0.9 | 0.54
| top | 2 | 13.2 | 0.45 | 0.333 | 3.96
|  | 1 | 4.4 | 0.45 | 0.333 | 0.66
| chamber | 4 | 0.9 | 0.1 | 0.9 | 0.32
| cover | 1 | 1 | 1 | 0.1 | 0.1
| less | -1 | 0.6 | 0.6 | 0.1 | -0.04
Goldhunga
| Base Slab | 1 | 10.5 | 4 | 0.18 | 7.56
| long wall | 2 | 10.35 | 0.15 | 2.8 | 8.69
| shortwall | 2 | 3.85 | 0.15 | 2.8 | 3.23 |  | 10.35
| outlet dedn | -1 | 3.4 | 0.15 | 0.2 | -0.1 |  | 3.45
| inlet | 1 | 3.6 | 0.55 | 0.075 | 0.15
| outlet | 1 | 3.4 | 0.55 | 0.075 | 0.14
| medium wall | 1 | 3.6 | 0.15 | 2 | 1.08
| baffle wall | 1 | 3.4 | 0.15 | 0.9 | 0.46
| top | 2 | 11.4 | 0.45 | 0.333 | 3.42
|  | 1 | 4 | 0.45 | 0.333 | 0.6
[6 empty] | 86.36 | m3
8 | Centring and Shuttering Works for
P.C.C. and R.C.C Works, PST
Dham
| Base Slab | 2 | 12.4 |  | 0.18 | 4.464
|  | 2 | 4.4 |  | 0.18 | 1.584
| long wall | 4 | 12.25 |  | 2.8 | 137.2
| shortwall | 4 | 4.25 |  | 2.8 | 47.6
| outlet dedn | -1 | 3.7 |  | 0.2 | -0.74
| inlet | 1 | 4 | 0.55 |  | 2.2
| outlet | 1 | 3.7 | 0.55 |  | 2.035
| medium wall | 2 | 4 |  | 2 | 16
| baffle wall | 2 | 4 |  | 0.9 | 7.2
| top | 2 | 13.3 | 0.45 |  | 11.97
|  | 1 | 4.4 | 0.45 |  | 1.98
Ranatole
| Base Slab | 2 | 12.3 |  | 0.18 | 4.428
|  | 2 | 4.4 |  | 0.18 | 1.584
| long wall | 4 | 12.15 |  | 2.8 | 136.08
| shortwall | 4 | 4.25 |  | 2.8 | 47.6
| outlet dedn | -1 | 3.7 |  | 0.2 | -0.74
| inlet | 1 | 4 | 0.55 |  | 2.2
| outlet | 1 | 3.7 | 0.55 |  | 2.035
| medium wall | 2 | 4 |  | 2 | 16
| baffle wall | 2 | 4 |  | 0.9 | 7.2
| top | 2 | 13.2 | 0.45 |  | 11.88
|  | 1 | 4.4 | 0.45 |  | 1.98
Goldhunga
| Base Slab | 2 | 10.5 |  | 0.18 | 3.78
|  | 2 | 4 |  | 0.18 | 1.44
| long wall | 4 | 10.35 |  | 2.8 | 115.92
| shortwall | 4 | 3.85 |  | 2.8 | 43.12
| outlet dedn | -1 | 3.4 |  | 0.2 | -0.68
| inlet | 1 | 3.6 | 0.55 |  | 1.98
| outlet | 1 | 3.4 | 0.55 |  | 1.87
| medium wall | 2 | 3.6 |  | 2 | 14.4
| baffle wall | 2 | 3.4 |  | 0.9 | 6.12
| top | 2 | 11.4 | 0.45 |  | 10.26
|  | 1 | 4 | 0.45 |  | 1.8
|  |  |  | Total |  | 661.75 | m2
9 | Reiforcement Works with Deformed
bars Including supplying, Cutting,
Bending and Placing in Position
Dham
Base Slab
| Main bar 12 mm dia at 175mm c/c Hor top | 77 | 6.42 | 0.88171 | kg/m | 435.87
| Dist bar 10 mm dia at 200mm c/c Hor top | 28 | 14.22 | 0.6123 | kg/m | 243.79
| Main bar 12 mm dia at 175 mm c/c Hor bot | 77 | 6.42 | 0.88171 | kg/m | 435.87
| Dist bar 10 mm dia at 200 mm c/c Hor bot | 28 | 14.22 | 0.6123 | kg/m | 243.79
Haunch Bar
| Haunch bar 12 mm dia at 200mm c/c diag | 135 | 1.2 | 0.88171 | kg/m | 142.84
| Haunch bar 12 mm dia at 200mm c/c diag | 55 | 1.2 | 0.88171 | kg/m | 58.19
[6 empty] | 1560.35 | kg
Long Walls
| Main bar inner 12 mm dia 150mm c/c verIF | 167 | 3.18 | 0.88171 | kg/m | 468.24
| Dist bar 10 mm dia at 300 mm c/c Hor IF | 18 | 13.32 | 0.6123 | kg/m | 146.81
| Main bar outer 12 mm dia200mm c/c verOF | 126 | 3.18 | 0.88171 | kg/m | 353.28
| Dist bar 10 mm dia at 300 mm c/c Hor OF | 18 | 13.32 | 0.6123 | kg/m | 146.81
[6 empty] | 1115.14 | kg
Short Wall
| Main bar inner 12 mm dia200 mm c/c Hor IF | 26 | 4.92 | 0.88171 | kg/m | 112.79
| Dist bar 10 mm dia 300 mm c/c ver IF | 31 | 32.58 | 0.6123 | kg/m | 618.41
| Main bar outer 12mm dia 200mm c/c HorOF | 26 | 4.92 | 0.88171 | kg/m | 112.79
| Dist bar 10 mm dia at 300 mm c/c Hor OF | 31 | 32.58 | 0.6123 | kg/m | 618.41
[6 empty] | 1462.4 | kg
| Main bar both face up to 1m ht 12mm dia 200mm c/c ver | 341 | 1.78 | 0.88171 | kg/m | 535.18
Channel
| Main bar 10 mm @ 150 mm c/c | 29 | 1 | 0.6123 | kg/m | 17.76
| Distribution bar 10 mm @ 100 mm c/c | 14 | 4.16 | 0.6123 | kg/m | 35.66
| Baffle bottom | 25 | 0.75 | 0.6123 | kg/m | 11.48
| Baffle wall | 25 | 1 | 0.6123 | kg/m | 15.31
80.21
| Corner bars 12 mm dia @ 200 mm c/c | 52 | 3.504 | 0.88171 | kg/m | 160.65
|  |  |  | Sub Total |  | 4913.93 | kg
| Ranatole |  |  |  |  | 4913.93 | kg
Goldhunga
Base Slab
| Main bar 12 mm dia at 175mm c/c Hor top | 65 | 6 | 0.88171 | kg/m | 343.87
| Dist bar 10 mm dia at 200mm c/c Hor top | 24 | 12.22 | 0.6123 | kg/m | 179.58
| Main bar 12 mm dia at 175 mm c/c Hor bot | 65 | 6 | 0.88171 | kg/m | 343.87 |  | 13.3333
| Dist bar 10 mm dia at 200 mm c/c Hor bot | 24 | 12.42 | 0.6123 | kg/m | 182.51
Haunch Bar
| Haunch bar 12 mm dia at 200mm c/c diag | 110 | 1.2 | 0.88171 | kg/m | 116.39
| Haunch bar 12 mm dia at 200mm c/c diag | 40 | 1.2 | 0.88171 | kg/m | 42.32
[6 empty] | 1208.54 | kg
Long Walls
| Main bar inner 12 mm dia 150mm c/c verIF | 150 | 3.18 | 0.88171 | kg/m | 420.58
| Dist bar 10 mm dia at 300 mm c/c Hor IF | 18 | 11.5 | 0.6123 | kg/m | 126.75
| Main bar outer 12 mm dia200mm c/c verOF | 105 | 3.18 | 0.88171 | kg/m | 294.4
| Dist bar 10 mm dia at 300 mm c/c Hor OF | 18 | 13.32 | 0.6123 | kg/m | 146.81
[6 empty] | 988.54 | kg
Short Wall
| Main bar inner 12 mm dia200 mm c/c Hor IF | 26 | 4.92 | 0.88171 | kg/m | 112.79
| Dist bar 10 mm dia 300 mm c/c ver IF | 31 | 32.58 | 0.6123 | kg/m | 618.41
| Main bar outer 12mm dia 200mm c/c HorOF | 26 | 4.92 | 0.88171 | kg/m | 112.79
| Dist bar 10 mm dia at 300 mm c/c Hor OF | 31 | 32.58 | 0.6123 | kg/m | 618.41
[6 empty] | 1462.4 | kg
| Main bar both face up to 1m ht 12mm dia 200mm c/c ver | 288 | 1.78 | 0.88171 | kg/m | 452
Channel
| Main bar 10 mm @ 150 mm c/c | 24 | 1 | 0.6123 | kg/m | 14.7
| Distribution bar 10 mm @ 100 mm c/c | 10 | 4.16 | 0.6123 | kg/m | 25.47
| Baffle bottom | 20 | 0.75 | 0.6123 | kg/m | 9.18
| Baffle wall | 20 | 1 | 0.6123 | kg/m | 12.25
61.6
| Corner bars 12 mm dia @ 200 mm c/c | 45 | 3.504 | 0.88171 | kg/m | 139.03
|  |  |  | Sub Total |  | 4312.11 | kg
| Net Reinforcement |  |  | Total |  | 14139.97 | kg
10 | Brick Masonry Work in 1:6 Cement Sand
|  |  |  | Total |  | 0
11 | 12.5 mm Thick Cement Sand Plaster
in 1:3 Mortar with 2% Water Proof
Dham
| Base slab | 1 | 12.05 |  | 4.05 | 48.8025
| long wall | 2 | 12.05 |  | 2.9 | 69.89
| short wall | 2 | 4.05 |  | 2.9 | 23.49
| dedn | -2 | 0.17 |  | 2 | -0.68
|  | -2 | 0.17 |  | 0.9 | -0.306
| wall in between | 2 | 4 |  | 2.075 | 16.6
| Baffle wall | 2 | 4 |  | 0.9
| inlet and outlet | 2 | 3.6 | 0.65 |  | 4.68
ranatole
| Base slab | 1 | 12 |  | 4.05 | 48.6
| long wall | 2 | 12 |  | 2.9 | 69.6
| short wall | 2 | 4.05 |  | 2.9 | 23.49
| dedn | -2 | 0.17 |  | 2 | -0.68
|  | -2 | 0.17 |  | 0.9 | -0.306
| wall in between | 2 | 4 |  | 2.075 | 16.6
| Baffle wall | 2 | 4 |  | 0.9
| inlet and outlet | 2 | 3.6 | 0.65 |  | 4.68
goldhunga
| Base slab | 1 | 10.15 |  | 3.65 | 37.0475
| long wall | 2 | 10.15 |  | 2.9 | 58.87
| short wall | 2 | 3.65 |  | 2.9 | 21.17
| dedn | -2 | 0.17 |  | 2 | -0.68
|  | -2 | 0.17 |  | 0.9 | -0.306
| wall in between | 2 | 3.65 |  | 2.075 | 15.1475
| Baffle wall | 2 | 3.65 |  | 0.9
| inlet and outlet | 2 | 2.95 | 0.65 |  | 3.835
|  |  |  | Total |  | 459.5445 | m2
12 | 12.5 mm Thick Cement Sand Plaster in
1:4 Mortar
dham
| outer side | 2 | 12.4 |  | 3.25 | 80.6
|  | 2 | 4.4 |  | 3.25 | 28.6
Ranatole
| outer side | 2 | 12.3 |  | 3.25 | 79.95
|  | 2 | 4.4 |  | 3.25 | 28.6
goldhunga
| outer side | 2 | 10.5 |  | 3.25 | 68.25
|  | 2 | 4 |  | 3.25 | 26
|  |  |  | Total |  | 312 | m2
13 | 3 mm Thick Punning in 1: 1 Cement
| Sand Mortar | inner plastered surfaces of SSF and CWC |  |  |  | 459.5445 | m2
|  |  |  | Total |  | 459.5445 | m2
14 | Two Coat of Enamel Paint of
| Appropriate Colour on Exposed | Outer plastered surfaces of SSF and CWC
| Surface of Tank |  |  |  |  | 312 | m2
15 | Installation of 5 inch dia. Pipe
Pieces and Fittings for Inlet, Outlet and W/O Complete as per Drawing
| and Specification | lumpsum |  |  |  | L.S.
16 | Standard Manhole Cover (60cm dia)
including M.S. Angle of 1.5" in
Size including Fixing all Complete as
| per Drawing and Specification | 3 |  |  |  | 3 | Nos.

## fencing quantity (hidden)
Shankharapur Municipaltiy Office
Office of Municipal Executuve
Bagmati Pradesh, Sankhu Kathmandu
Detail Measurement Sheet
Bill No: Final Bill
Contractor Name: SMO/079/80/84
Contractor's Name: Goldenstar Construction and Suppliers pvt. Ltd. ,Madhyapur thimi-3
Project: Construction of semi underground water tanks and sedimentaion tanks, Manichood Khanepani | [6 empty] | F/Y: 079/80
Location: Shankharapur-8 | [6 empty] | Date: 2080/3/21
Component: BARBED WIRE FENCING
S.N. | Description of Works | No | Length (m) | Breadth (m) | Height (m) | Quantity | Units | Remarks
BARBED WIRE FENCING
2 | Earthwork in excavation pillars
| dham retaining wall | 1 | 14.4 | 0.45 | 0.3 | 1.944
|  | 1 | 26\ | 0.45 | 0.6 | 0.27
|  | 1 | 5 | 0.6 | 0.6 | 1.8
|  | 1 | 13.5 | 0.45 | 0.6 | 3.645
|  | 1 | 12.2 | 0.45 | 0.6 | 3.294
|  | 1 | 7.5 | 0.45 | 0.6 | 2.025
| Ranatole | 1 | 46 | 0.4 | 0.6 | 11.04
[6 empty] | 24.02 | m³
3 | Dry stone soling with sand pillars
| dham retaining wall | 1 | 14.4 | 0.45 | 0.15 | 0.972
|  | 1 | 26\ | 0.5 | 0.15 | 0.075
|  | 1 | 5 | 0.6 | 0.15 | 0.45
|  | 1 | 13.5 | 0.45 | 0.15 | 0.91125
|  | 1 | 12.2 | 0.5 | 0.15 | 0.915
|  | 1 | 7.5 | 0.45 | 0.15 | 0.50625
| Ranatole | 1 | 46 | 0.45 | 0.15 | 3.105
[6 empty] | 6.93 | m³
4 | PCC (1:2:4) for anchor blocks
| dham retaining wall | 1 | 14.4 | 0.45 | 0.05 | 0.324
|  | 1 | 26\ | 0.5 | 0.05 | 0.025
|  | 1 | 5 | 0.6 | 0.05 | 0.15
|  | 1 | 13.5 | 0.45 | 0.05 | 0.30375
|  | 1 | 12.2 | 0.5 | 0.05 | 0.305
|  | 1 | 7.5 | 0.45 | 0.05 | 0.16875
| Ranatole | 1 | 46 | 0.45 | 0.05 | 1.035
[6 empty] | 2.3115 | m³
5 | Stone masonry (1:6) cement mortar Pillars | [7 empty] | 0 | 60
| dham retaining wall | 1 | 14.4 | 0.45 | 1.1 | 7.128
|  | 1 | 26\ | 0.5 | 1.2 | 0.6
|  | 1 | 5 | 0.6 | 2.5 | 7.5
|  | 1 | 13.5 | 0.45 | 1.2 | 7.29
|  | 1 | 12.2 | 0.5 | 1.2 | 7.32 |  |  | 12.2 | 40
|  | 1 | 7.5 | 0.45 | 0.3 | 1.0125
52.6
| Ranatole | 1 | 46 | 0.45 | 1.35 | 27.945
[6 empty] | 58.8 | m³ |  | 12.2
6 | Barbed wire fencing (16+1: one more lengths of barbed
wire to be anchored on entrance gate).
Cross Barbed Wire
| dham | 1 | 806.4 |  |  | 806.4
|  | 1 | 248.16 |  |  | 248.16
| Ranatole | 1 | 672 |  |  | 672
|  | 1 | 56.4 |  |  | 56.4
[6 empty] | 1782.96 | m
7 | 6 mm ø mild steel rod for hooks, 650 mm long each
[6 empty] | 0 | kg
8 | M.S. 40 x 40 x 6 angle bar, 2.5 m long
| Dham | 44 | 2.5 | 3.5 | kg/unit | 385
| Ranatole | 20 | 2.5 | 3.5 | kg/unit | 175
[6 empty] | 560 | kg

## truck ana (hidden)
Analysis of Transportation cost
from
Truck Analysis
| Cost of truck : -With VAT | [5 empty] | 3164000 | Rs.
| -Without VAT | [5 empty] | 2800000 | Rs.
| Total working period | [5 empty] | 10000 | hr.
| Yearly working period | [5 empty] | 2000 | hr.
1 | Proprietory cost
| a) Depreciation value |  | cost of truck / working period |  |  |  | 280 | Rs./hour
| b) Insurance cost |  | 2% of (cost of truck / yearly
|  |  | working period) |  |  |  | 28 | Rs./hour
| c) Interest |  | 1% of (cost of truck / yearly
|  |  | working period) |  |  |  | 14 | Rs./hour
|  |  | Subtotal |  |  |  | 322 | Rs./hour
2 | Operation expenses
2.1 | Repair & Maintennance cost
| a) Overhauling cost |  | 55% of 1(a) |  |  |  | 154 | Rs./hour
| b) Repair & maintennance cost |  | 23% of 1(a) |  |  |  | 64.4 | Rs./hour
|  |  | Subtotal |  |  |  | 218.4
2.2 | Actual operation cost
a) Cost of fuel and lubrication
| H.S.D. |  | 5.5 | L @ | 65 | Rs/L | 357.5 | Rs./hour
| Mobil |  | 0.1 | L @ | 580.26 | Rs/L | 58.03 | Rs./hour
| Gear oil |  | 0.03 | L @ | 580.26 | Rs/L | 17.41 | Rs./hour
| Grease |  | 0.015 | kg @ | 640.15 | Rs/kg | 9.6 | Rs./hour
|  |  | Subtotal |  |  |  | 442.54 | Rs./hour
b) Extra machinery parts
|  | Life of tyre = | 2000 | hr
|  | Cost of tyre with VAT = | 22400.25 | Rs.
|  | Cost of tyre without VAT = | 19823.2301 | Rs.
|  | Cost of tyre per hour | cost of tyre/life x 6 |  |  |  | 59.47 | Rs./hour
| Other parts at lump- sump | [5 empty] | 8.4 | Rs./hour
| Other expenses at lump- sump | [5 empty] | 2.8 | Rs./hour
|  |  | Subtotal |  |  |  | 70.67 | Rs./hour
c) Salary
| Salary of driver |  | 500 | Rs/day |  |  | 62.5
| Salary of asistant |  | 300 | Rs/day |  |  | 37.5
| Loading / unloading |  | incorporated in transportation rate |  |  |  | 0
|  |  | Subtotal |  |  |  | 100 | Rs./hour
| d)Improve & small repair works | [5 empty] | 16.8 | Rs./hour
| Hence actual operation cost |  | 2.1+2.2(a)+2.2(b)+2.2(c)+2.2(d) |  |  |  | 848.41 | Rs./hour
3 | Supervision and overhead cost
|  |  | @ 5% of cost of truck / yearly working hour |  |  |  | 70 | Rs./hour
| Total expenses in transportation by truck per hour |  |  | 1+2+3 |  |  | 1240.41 | Rs./hour
Assuming speed of truck as 8 km/hr in eathen, 12 km/hr in gravel, and 20 km/hr in metalled road :
Using the formula , the rate of transportation comes to be :
| Rate /kg= |  | ( 2x distance/truck speed+0.75) x total expence /6000
Rate/km.quintal
| Type of road |  | Distance,km | Time, hr |  | Convenient | Inconvenient
| Earthen road |  | 0 | 0 |  | 0 | 0
| Gravel road |  | 0 | 0 |  | 0 | 0
| Metalled road |  | 0 | 0 |  | 0 | 0

## fe-Rt quant (hidden)
Quantity of
Ferrocement Tanks
S.N. | Description | Unit | Unit Rate |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 12 | 14 | 16 | 18 | 20 | 1 m3 | 2 m3 | 3 m3 | 4 m3 | 5 m3 | 6 m3 | 7 m3 | 8 m3 | 9 m3 | 10 m3 | 12 m3 | 14 m3 | 16 m3 | 18 m3 | 20 m3
1 | Site clearance | m² | 137.54 | 35 | 24 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 48 | 48 | 48 | 48 | 3300.96 | 3300.96 | 3300.96 | 3300.96 | 4813.9 | 4813.9 | 4813.9 | 4813.9 | 4813.9 | 4813.9 | 4813.9 | 6601.92 | 6601.92 | 6601.92 | 6601.92
2 | Earthwork in excavation in boulder mixed soil | m³ | 1732.69 | 21.8 | 9.36 | 13.13 | 14.52 | 17.57 | 19.16 | 21.8 | 23.78 | 26.42 | 26.59 | 29.08 | 33.23 | 36.01 | 40.09 | 41.5 | 45.19 | 16217.9784 | 22750.2197 | 25158.6588 | 30443.3633 | 33198.3404 | 37772.642 | 41203.3682 | 45777.6698 | 46072.2271 | 50386.6252 | 57577.2887 | 62394.1669 | 69463.5421 | 71906.635 | 78300.2611
3 | Earthwork in excavation in hard soil | m³ | 653.84 | 7.1 | 1.66 | 4.43 | 4.03 | 6.04 | 5.52 | 7.1 | 8.29 | 9.86 | 8.17 | 9.52 | 11.79 | 11.27 | 13.33 | 12 | 13.72 | 1085.3744 | 2896.5112 | 2634.9752 | 3949.1936 | 3609.1968 | 4642.264 | 5420.3336 | 6446.8624 | 5341.8728 | 6224.5568 | 7708.7736 | 7368.7768 | 8715.6872 | 7846.08 | 8970.6848
4 | Stone soling | m³ | 5141.87 | 1.75 | 0.93 | 0.93 | 1.3 | 1.3 | 1.75 | 1.75 | 1.75 | 1.75 | 2.28 | 2.28 | 2.28 | 2.88 | 2.88 | 3.56 | 3.56 | 4781.9391 | 4781.9391 | 6684.431 | 6684.431 | 8998.2725 | 8998.2725 | 8998.2725 | 8998.2725 | 11723.4636 | 11723.4636 | 11723.4636 | 14808.5856 | 14808.5856 | 18305.0572 | 18305.0572
5 | Stone masonry in 1:6 c-s mortar | m³ | 14084.92 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 2.01 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892 | 28310.6892
6 | Plain cement concrete (1:2:4) in sub-structure | m³ | 15694.9 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 0.395 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855 | 6199.4855
7 | Plain cement concrete (1:1.5:3) sub-structure | m³ | 16948.41 | 0.77 | 0.318 | 0.318 | 0.519 | 0.519 | 0.77 | 0.77 | 0.77 | 0.77 | 1.069 | 1.069 | 1.069 | 1.418 | 1.418 | 1.815 | 1.815 | 5389.5944 | 5389.5944 | 8796.2248 | 8796.2248 | 13050.2757 | 13050.2757 | 13050.2757 | 13050.2757 | 18117.8503 | 18117.8503 | 18117.8503 | 24032.8454 | 24032.8454 | 30761.3641 | 30761.3641
8 | Steel reinforcement | kg | 123.56 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856 | 1556.856
9 | Centering & shuttering work for concreting | m² | 1278.27 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932 | 1482.7932
10 | HDPE pipe-formwork for ferro-cement work | m² | 459.51 | 17.38 | 6.3 | 8.75 | 11.29 | 13.23 | 15.78 | 17.38 | 18.59 | 20.2 | 22.25 | 23.69 | 26.1 | 29.78 | 32.02 | 35.2 | 37.11 | 2894.913 | 4020.7125 | 5187.8679 | 6079.3173 | 7251.0678 | 7986.2838 | 8542.2909 | 9282.102 | 10224.0975 | 10885.7919 | 11993.211 | 13684.2078 | 14713.5102 | 16174.752 | 17052.4161
11 | Bar binding works including chicken wire, steel bars, GI plain wires, etc | m² | 1222.5 | 17.38 | 6.3 | 8.75 | 11.29 | 13.23 | 15.78 | 17.38 | 18.59 | 20.2 | 22.25 | 23.69 | 26.1 | 29.78 | 32.02 | 35.2 | 37.11 | 7701.75 | 10696.875 | 13802.025 | 16173.675 | 19291.05 | 21247.05 | 22726.275 | 24694.5 | 27200.625 | 28961.025 | 31907.25 | 36406.05 | 39144.45 | 43032 | 45366.975
12 | 12.5 mm thick 1:2 c-s plaster | m² | 527.79 | 69.54 | 25.18 | 34.98 | 45.11 | 52.88 | 63.11 | 69.54 | 74.37 | 80.8 | 88.97 | 94.74 | 104.35 | 119.1 | 128.05 | 140.75 | 148.41 | 13289.7522 | 18462.0942 | 23808.6069 | 27909.5352 | 33308.8269 | 36702.5166 | 39251.7423 | 42645.432 | 46957.4763 | 50002.8246 | 55074.8865 | 62859.789 | 67583.5095 | 74286.4425 | 78329.3139
13 | 12.5 mm thick 1:3 c-s plaster | m² | 485.7 | 4.91 | 1.77 | 1.77 | 3.14 | 3.14 | 4.91 | 4.91 | 4.91 | 4.91 | 7.07 | 7.07 | 7.07 | 9.62 | 9.62 | 12.57 | 12.57 | 859.689 | 859.689 | 1525.098 | 1525.098 | 2384.787 | 2384.787 | 2384.787 | 2384.787 | 3433.899 | 3433.899 | 3433.899 | 4672.434 | 4672.434 | 6105.249 | 6105.249
14 | 12.5 mm thick 1:4 c-s plaster | m² | 478.27 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 4.94 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538 | 2362.6538
15 | 3 mm thick 1:1 c-s punning | m² | 332.33 | 16.69 | 6.01 | 8.37 | 10.68 | 12.56 | 15.12 | 16.69 | 17.87 | 19.44 | 21.21 | 22.62 | 24.98 | 28.31 | 30.51 | 33.3 | 35.19 | 1997.3033 | 2781.6021 | 3549.2844 | 4174.0648 | 5024.8296 | 5546.5877 | 5938.7371 | 6460.4952 | 7048.7193 | 7517.3046 | 8301.6034 | 9408.2623 | 10139.3883 | 11066.589 | 11694.6927
16 | Two coats of bitumen paint | m² | 97.89 | 8.98 | 2.51 | 5.03 | 5.28 | 7.26 | 7.35 | 8.98 | 10.21 | 11.84 | 10.71 | 12.17 | 14.61 | 14.7 | 16.96 | 16.1 | 18.03 | 245.7039 | 492.3867 | 516.8592 | 710.6814 | 719.4915 | 879.0522 | 999.4569 | 1159.0176 | 1048.4019 | 1191.3213 | 1430.1729 | 1438.983 | 1660.2144 | 1576.029 | 1764.9567
17 | Two coats of snowcem paint | m² | 200.01 | 9.08 | 4.31 | 4.31 | 6.61 | 6.61 | 9.08 | 9.08 | 9.08 | 9.08 | 12.23 | 12.23 | 12.23 | 15.83 | 15.83 | 19.88 | 19.88 | 862.0431 | 862.0431 | 1322.0661 | 1322.0661 | 1816.0908 | 1816.0908 | 1816.0908 | 1816.0908 | 2446.1223 | 2446.1223 | 2446.1223 | 3166.1583 | 3166.1583 | 3976.1988 | 3976.1988
18 | Standard manhole cover - circular(600Ø) | set | 1000 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
19 | Installation of pipes & fittings | job | 500 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
20 | Barbed wire fencing (Type-A) | m | 2445.48 | 21 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 24 | 24 | 24 | 24 | 24 | 24 | 44018.64 | 44018.64 | 44018.64 | 44018.64 | 51355.08 | 51355.08 | 51355.08 | 51355.08 | 51355.08 | 58691.52 | 58691.52 | 58691.52 | 58691.52 | 58691.52 | 58691.52
21 | Entrancce gate in barbed wire fencing (Type-A) | no | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 163725.7447 | [13 empty] | 145058.1185 | 163725.7447 | 182718.175 | 197499.7282 | 227233.6867 | 239607.28 | 248913.0877 | 261296.9627 | 278196.2128 | 296808.6823 | 315632.419 | 347946.1768 | 365806.2427 | 392742.3144 | 408333.0872

## data (hidden)
For GI pipe : costing and transportation |  |  |  |  | Design of Ferrocement Tank
|  | Weight per m | Rate per m |  | RT size(m³) | Dome Height(m) | Total tank height(m) | inner diameter of Tank(m) | fencing length(m)
15 | GI (Medium) | 1.284 | 172 |  | 1 | 0.3 | 0.9 | 1.5 | 18
20 | GI (Medium) | 1.658 | 220 |  | 2 | 0.3 | 1.4 | 1.5 | 18
25 | GI (Medium) | 2.53 | 328 |  | 3 | 0.4 | 1.2 | 2 | 18
32 | GI (Medium) | 3.279 | 427 |  | 4 | 0.4 | 1.5 | 2 | 18
40 | GI (Medium) | 3.788 | 490 |  | 5 | 0.4 | 1.3 | 2.5 | 21
50 | GI (Medium) | 5.319 | 670 |  | 6 | 0.4 | 1.5 | 2.5 | 21
65 | GI (Medium) | 6.349 | 855 |  | 7 | 0.4 | 1.65 | 2.5 | 21
80 | GI (Medium) | 8.85 | 1060 |  | 8 | 0.4 | 1.85 | 2.5 | 21
100 | GI (Medium) | 12.99 | 1573 |  | 9 | 0.5 | 1.5 | 3 | 21
125 | GI (Medium) | 16.95 | 2180 |  | 10 | 0.5 | 1.65 | 3 | 24
150 | GI (Medium) | 20 | 2633 |  | 12 | 0.5 | 1.9 | 3 | 24
[5 empty] | 14 | 0.6 | 1.7 | 3.5 | 24
[5 empty] | 16 | 0.6 | 1.9 | 3.5 | 24
15 | GI (Heavy) | 1.513 | 203 |  | 18 | 0.7 | 1.65 | 4 | 24
20 | GI (Heavy) | 1.969 | 257 |  | 20 | 0.7 | 1.8 | 4 | 24
25 | GI (Heavy) | 3.077 | 383
32 | GI (Heavy) | 3.968 | 490
40 | GI (Heavy) | 4.587 | 565
50 | GI (Heavy) | 6.369 | 823
65 | GI (Heavy) | 8.197 | 1032
80 | GI (Heavy) | 10.417 | 1215
100 | GI (Heavy) | 15.436 | 1883
125 | GI (Heavy) | 18.52 | 2440
150 | GI (Heavy) | 22.22 | 2767
Data relating to HDPE pipes
Code | External Dia | Pressure rating | Weight/m | Inner dia(bore)
26 | 16 | 10 | 0.092 | 11.6
30 | 20 | 10 | 0.134 | 14.9
35 | 25 | 10 | 0.202 | 18.9
38 | 32 | 6 | 0.226 | 26.9
42 | 32 | 10 | 0.334 | 24.1
44 | 40 | 4 | 0.251 | 35.6
46 | 40 | 6 | 0.35 | 33.7
50 | 40 | 10 | 0.514 | 30.3
54 | 50 | 4 | 0.378 | 44.7
56 | 50 | 6 | 0.542 | 42.2
60 | 50 | 10 | 0.796 | 38
65.5 | 63 | 2.5 | 0.403 | 58.6
67 | 63 | 4 | 0.585 | 56.5
69 | 63 | 6 | 0.85 | 53.3
73 | 63 | 10 | 1.269 | 47.8
77.5 | 75 | 2.5 | 0.557 | 69.9
79 | 75 | 4 | 0.846 | 67.1
81 | 75 | 6 | 1.191 | 63.6
85 | 75 | 10 | 1.782 | 57.1
92.5 | 90 | 2.5 | 0.799 | 83.9
94 | 90 | 4 | 1.22 | 80.5
96 | 90 | 6 | 1.715 | 76.3
100 | 90 | 10 | 2.568 | 68.5
112.5 | 110 | 2.5 | 1.185 | 102.6
114 | 110 | 4 | 1.703 | 99.2
116 | 110 | 6 | 2.545 | 93.4
120 | 110 | 10 | 3.801 | 84
127.5 | 125 | 2.5 | 1.53 | 116.6
129 | 125 | 4 | 2.289 | 112.2
131 | 125 | 6 | 3.293 | 106.1
135 | 125 | 10 | 4.962 | 95.1
142.5 | 140 | 2.5 | 1.897 | 130.7
144 | 140 | 4 | 2.901 | 125.5
146 | 140 | 6 | 4.15 | 118.7
150 | 140 | 10 | 6.209 | 106.6
162.5 | 160 | 2.5 | 2.453 | 149.5
164 | 160 | 4 | 3.773 | 143.5
166 | 160 | 6 | 5.355 | 136
170 | 160 | 10 | 8.079 | 122
182.5 | 180 | 2.5 | 3.148 | 168
184 | 180 | 4 | 4.762 | 161.5
186 | 180 | 6 | 6.8 | 152.9
190 | 180 | 10 | 10.256 | 137.1
202.5 | 200 | 2.5 | 3.875 | 186.7
204 | 200 | 4 | 5.89 | 179.4
206 | 200 | 6 | 8.391 | 169.9
210 | 200 | 10 | 12.62 | 152.5
227.5 | 225 | 2.5 | 4.822 | 210.3
229 | 225 | 4 | 7.445 | 201.8
231 | 225 | 6 | 10.544 | 191.4
235 | 225 | 10 | 16.014 | 171.4
252.5 | 250 | 2.5 | 6.012 | 233.5
254 | 250 | 4 | 9.187 | 224.3
256 | 250 | 6 | 13.041 | 212.6
260 | 250 | 10 | 19.757 | 190.4
282.5 | 280 | 2.5 | 7.471 | 261.7
284 | 280 | 4 | 11.455 | 251.4
286 | 280 | 6 | 16.327 | 238.2
290 | 280 | 10 | 24.708 | 213.5

## Sheet2 (hidden)
Provisional Sum Items
S.No. | Description of Works | Unit | Quantity | Rate | Amount | Remarks
1 | 4" GI Nipple | nos | 3 | 2400 | 7200
2 | 4" GI Socket | nos | 4 | 925 | 3700
3 | 4" GI Sluice Valve | nos | 3 | 14000 | 42000
4 | 4" GI Plug | nos | 4 | 500 | 2000
5 | 3" GI Elbow | nos | 9 | 850 | 7650
6 | 3" GI Plug | nos | 5 | 500 | 2500
7 | 3" GI Socket | nos | 5 | 525 | 2625
8 | 2-1/2 GI Socket | nos | 5 | 360 | 1800
9 | 2-1/2 GI Plug | nos | 5 | 200 | 1000
10 | 3/4x 3" long GI Nipple | nos | 3 | 50 | 150
11 | 3/4x 9" long GI Nipple | nos | 3 | 150 | 450
12 | 3/4 GI socket | nos | 6 | 60 | 360
13 | 3/4 GI Union | nos | 3 | 157 | 471
14 | 3/4 GI Gate Valve | nos | 3 | 1050 | 3150
15 | 3/4 x 4 GI Nipple | nos | 7 | 64 | 448
16 | 3/4 x 6 GI Nipple | nos | 2 | 100 | 200
17 | 4"x6.5' GI Nipple Pipe | nos | 3 | 10712 | 32136
18 | 4x24" nipple Pipe | nos | 4 | 3113 | 12452
19 | 3" x 6.5' GI pipe nipple | nos | 1 | 7452 | 7452
20 | 3x4 Nipple | nos | 9 | 480 | 4320
21 | 3" x 6.5' GI pipe nipple | nos | 1 | 7452 | 7452
22 | 2-1/2 x 6.5' GI Nipple | nos | 2 | 5818 | 11636
23 | 2" x 6.5' long Nipple | nos | 2 | 4556 | 9112
24 | 3/4" x 6.5 ft Nipple | nos | 2 | 1490 | 2980
25 | 3/4" x 10" GI Nipple | nos | 6 | 2235 | 13410
|  |  |  | Total | 176654 | Rs
|  |  |  | VAT 13% | 22965.02 | Rs
|  |  |  | All total | 199619.02 | Rs
| previous bill amount (insurance extra) |  |  |  | 35494 | Rs
|  |  |  | Grand Total | 235113.02 | Rs

## Sheet3 (hidden)
Shankharapur Municipality
Office of Municipal Executive
Sankhu, Kathmandu
FInal Bill
| योजनाको नामः | Construction of semi underground water tanks and sedimentaion tanks, Manichood Khanepani | [6 empty] | बिलको क्रम सङ्ख्याः |  | 2
| योजना कार्यान्वयन हुने स्थानः | shankharapur-8 | [6 empty] | कार्य आदेश मितिः |  | 2079-05-11
| ठेकदारको नामः | Goldenstar Construction and Suppliers Pvt. Ltd. | [6 empty] | काम सम्पन्न गर्नु पर्ने मितिः |  | 2079-03-10
| ठेक्का पट्टाको सङ्केतः | SMO/079/80/84 | [6 empty] | म्याद थप मितिः
| नापी किताब नं | [7 empty] | काम सम्पन्न भएको मितिः
Item.No | Description of work | Unit | सम्झौता बमोजिम |  |  | हाल भएको काम |  | अगिल्लो बिलमा भएको काम |  | हाल सम्म भएको काम |  | बाकि काम
|  |  | परिमाण | दर | रकम |  |  | परिमाण | रकम | परिमाण | रकम
1 | Site Clearance-off rooting of small trees, bushes and removing of top soil for 3 semi underground reservoirs and 3 sedimentation tanks | m2 | 870.8 | 80 | 69664 | 206.4531 | 16516.2475 | 702.7995 | 56223.9604 | 909.2526 | 72740.2079 | 38.4526 | 4.4158
2 | Excavation work in Soft soils for semi underground water tanks and sedimentation tanks all complete as per specifications | m3 | 827.1 | 80 | 66168 | 259.5266 | 20762.1291 | 498.8358 | 39906.866 | 758.3624 | 60668.9951 | -68.7376 | -8.3107
3 | Earth work in refilling with ordinary hard soil in 15cm layers including water sprinking and compaction after each layer all complete | m3 | 165.8 | 100 | 16580 | 29.7551 | 2975.5088 | 67.5168 | 6751.6753 | 97.2718 | 9727.1841 | -68.5282 | -41.3318
4 | Boulder Soling with sand for the foundation of structures as per required specification all complete | m3 | 101.26 | 3200 | 324032 | 17.1193 | 54781.7552 | 68.3894 | 218846.2186 | 85.5087 | 273627.9738 | -15.7513 | -15.5553
5 | Stone masonry in 1:6 c/s mortar in valve chamber and boundary wall as per required specification all complete | m3 | 134.55 | 6000 | 807300 | -48.6488 | -291892.5 | 123.75 | 742500 | 75.1012 | 450607.5 | -59.4488 | -44.1834
6 | Providing and laying PCC(1:3:6) work as Lean Concrete for floor as per required specification for foundation of water tank and sedimentation tank all complete | m3 | 42.8 | 6600 | 282480 | 8.9256 | 58908.7959 | 26.597 | 175540.0577 | 35.5226 | 234448.8536 | -7.2774 | -17.0034
7 | Providing and laying of PCC (1:2:4) in RCC components in Valve chamber and in RRM works all complete | m3 | 13.98 | 8000 | 111840 | -5.5297 | -44237.6 | 12.39 | 99120 | 6.8603 | 54882.4 | -7.1197 | -50.9278
8 | Providing and laying of PCC (1:1.5:3) for RCC components with 2 % WPC in structutral components of water tank and sedimentation tank al complete | m3 | 206.51 | 12800 | 2643328 | 99.3247 | 1271356.0327 | 137.9563 | 1765840.1969 | 237.281 | 3037196.2296 | 30.771 | 14.9005
9 | Providing of Formwork for concreting work in water tank and sedimentaion tank as per drawing and specification all complete | m2 | 1260.37 | 250 | 315092.5 | 958.2987 | 239574.6847 | 429.342 | 107335.5035 | 1387.6408 | 346910.1882 | 127.2708 | 10.0979
10 | Providing of extra Scafolding work(support for top slab) in water tank | ls | 3 | 10000 | 30000 | 2 | 20000 | 1 | 10000 | 3 | 30000 | 0 | 0
11 | Cutting bending,placing in position and binding Reinforcement steel bar in bottom slab wall ring beam, spherical dome of the tank and valve chamber cover slab and bottom as well as walls of sedimentation tank according to the drawing and specification (Size and quantity of bars required are given in Drg | kg | 27572.68 | 110 | 3032994.8 | 12036.9087 | 1324059.9618 | 15197.4341 | 1671717.7523 | 27234.3429 | 2995777.7141 | -338.3371
12 | Brick Masonry Work in 1:6 cement sand mortar for sedimentation tank all complete | m3 | 7.86 | 11500 | 90390 | 0 | 0 | 0 | 0 | 0 | 0 | -7.86
13 | Providing 12.5mm inside plaster in 1:3 c/s mortar with 2% WPC for water tank and sedimentation tank | m2 | 1178.83 | 280 | 330072.4 | 1162.9948 | 325638.5436 | 0 | 0 | 1162.9948 | 325638.5436 | -15.8352
14 | Providing 12.5mm outside plaster in 1:4 c/m for water tank and sedimentation tank | m2 | 600.55 | 280 | 168154 | 626.21 | 175338.7891 | 0 | 0 | 626.21 | 175338.7891 | 25.66
15 | Providing 3mm punning with 1:1 c/s mortar for water tank and sedimentation tank | m2 | 894.58 | 100 | 89458 | 850.9948 | 85099.4799 | 0 | 0 | 850.9948 | 85099.4799 | -43.5852
16 | Providing Double coat Snowcem paint on exposed surface of structures | m2 | 317.04 | 120 | 38044.8 | 330.2463 | 39629.556 | 0 | 0 | 330.2463 | 39629.556 | 13.2063
17 | Providing 2 coats bitumen painting over unexposed surface on water tank | m2 | 376.18 | 120 | 45141.6 | 344.3264 | 41319.1691 | 0 | 0 | 344.3264 | 41319.1691 | -31.8536
18 | Providing Two Coat of Enamel Paint of Appropriate Colour on Exposed Surface of sedimentation Tank | m2 | 206.67 | 120 | 24800.4 | 312 | 37440 | 0 | 0 | 312 | 37440 | 105.33
19 | Supply and installation of outer and inner steel pipe ladders as directed by site Engineer | ls | 6 | 20000 | 120000 | 6 | 120000 | 0 | 0 | 6 | 120000 | 0
20 | 60 cm dia. MS MH cover including procuring transporting and fixing at place, | nos | 12 | 10000 | 120000 | 10 | 100000 | 0 | 0 | 10 | 100000 | -2
21 | Installation of Pipe fittings for water tanks | ls | 3 | 20000 | 60000 | 3 | 60000 | 0 | 0 | 3 | 60000 | 0
22 | Construction site cleareance, leak proof test and disinfection of reservoir all complete | ls | 3 | 20000 | 60000 | 3 | 60000 | 0 | 0 | 3 | 60000 | 0
23 | Supply of Fittings for outlet of water tanks , 2-1/2" Dia 2m long G.I. Nipple | pc | 6 | 5500 | 33000 | 6 | 33000 | 0 | 0 | 6 | 33000 | 0
24 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Nipple 30cm long | pc | 6 | 1600 | 9600 | 6 | 9600 | 0 | 0 | 6 | 9600 | 0
25 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I.Socket | pc | 3 | 500 | 1500 | 3 | 1500 | 0 | 0 | 3 | 1500 | 0
26 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Elbow | pc | 6 | 780 | 4680 | 6 | 4680 | 0 | 0 | 6 | 4680 | 0
27 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Strainer50 cm long | pc | 6 | 2200 | 13200 | 6 | 13200 | 0 | 0 | 6 | 13200 | 0
28 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia Sluice valve | pc | 6 | 80 | 480 | 6 | 480 | 0 | 0 | 6 | 480 | 0
29 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. Flange | set | 6 | 610 | 3660 | 6 | 3660 | 0 | 0 | 6 | 3660 | 0
30 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia G.I. /HDPE Flange | set | 6 | 1600 | 9600 | 6 | 9600 | 0 | 0 | 6 | 9600 | 0
31 | Supply of Fittings for outlet of water tanks ,2-1/2" Dia C.I. Plug . | pc | 6 | 230 | 1380 | 6 | 1380 | 0 | 0 | 6 | 1380 | 0
32 | Supply of Fittings for outlet of water tanks ,2-1/2"*3/4" GI Unequal Tee | pc | 3 | 1100 | 3300 | 3 | 3300 | 0 | 0 | 3 | 3300 | 0
33 | Supply of Fittings for outlet of water tanks ,3/4" GI nipple 2m long | pc | 6 | 1500 | 9000 | 6 | 9000 | 0 | 0 | 6 | 9000 | 0
34 | Supply of Fittings for outlet of water tanks ,3/4" GI nipple 1 m long | pc | 3 | 780 | 2340 | 3 | 2340 | 0 | 0 | 3 | 2340 | 0
35 | Supply of Fittings for outlet of water tanks ,3/4" GI nipple 0.35 m long | pc | 3 | 350 | 1050 | 3 | 1050 | 0 | 0 | 3 | 1050 | 0
36 | Supply of Fittings for outlet of water tanks ,3/4"GI elbow | pc | 12 | 110 | 1320 | 12 | 1320 | 0 | 0 | 12 | 1320 | 0
37 | Supply of Fittings for outlet of water tanks ,3/4"GI Socket | pc | 6 | 100 | 600 | 6 | 600 | 0 | 0 | 6 | 600 | 0
38 | Supply of Fittings for outlet of water tanks ,3/4"GIUnion | pc | 3 | 210 | 630 | 3 | 630 | 0 | 0 | 3 | 630 | 0
39 | Supply of Fittings for outlet of water tanks ,3/4" short nipple 4" | pc | 9 | 100 | 900 | 9 | 900 | 0 | 0 | 9 | 900 | 0
40 | Supply of Fittings for overflow of water tanks ,3" Dia 2m long G.I. Nipple | pc | 6 | 6900 | 41400 | 6 | 41400 | 0 | 0 | 6 | 41400 | 0
41 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Nipple 0.6 m long | pc | 3 | 1710 | 5130 | 3 | 5130 | 0 | 0 | 3 | 5130 | 0
42 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Elbow | pc | 6 | 1270 | 7620 | 6 | 7620 | 0 | 0 | 6 | 7620 | 0
43 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Socket | pc | 3 | 880 | 2640 | 3 | 2640 | 0 | 0 | 3 | 2640 | 0
44 | Supply of Fittings for overflow of water tanks ,3" Dia G.I. Plug . | pc | 3 | 460 | 1380 | 3 | 1380 | 0 | 0 | 3 | 1380 | 0
45 | Supply of Fittings for overflow of water tanks ,3" Dia G.I/HDPE.Flange Set. | Set | 3 | 1900 | 5700 | 3 | 5700 | 0 | 0 | 3 | 5700 | 0
46 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia 2m long G.I. Nipple | pc | 3 | 3000 | 9000 | 3 | 9000 | 0 | 0 | 3 | 9000 | 0
47 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I. Nipple 1m long | pc | 3 | 1500 | 4500 | 3 | 4500 | 0 | 0 | 3 | 4500 | 0
48 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I. Elbow | pc | 3 | 350 | 1050 | 3 | 1050 | 0 | 0 | 3 | 1050 | 0
49 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I. Socket | pc | 3 | 300 | 900 | 3 | 900 | 0 | 0 | 3 | 900 | 0
50 | Supply of Fittings for inlet of water tanks ,1-1/2"Dia G.I. Short nipple | pc | 9 | 230 | 2070 | 9 | 2070 | 0 | 0 | 9 | 2070 | 0
51 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia gate Valve | pc | 3 | 3500 | 10500 | 3 | 10500 | 0 | 0 | 3 | 10500 | 0
52 | Supply of Fittings for inlet of water tanks ,1-1/2"Dia G.I. Plug . | pc | 3 | 80 | 240 | 3 | 240 | 0 | 0 | 3 | 240 | 0
53 | Supply of Fittings for inlet of water tanks ,1-1/2" Dia G.I/HDPE.Flange Set. | pc | 6 | 1110 | 6660 | 6 | 6660 | 0 | 0 | 6 | 6660 | 0
54 | Supply of Fittings for washout of water tanks ,3" Dia 2.8 m long G.I. Nipple | Pc | 3 | 9000 | 27000 | 3 | 27000 | 0 | 0 | 3 | 27000 | 0
55 | Supply of Fittings for washout of water tanks ,3" Dia G.I. Elbow | pc | 3 | 1100 | 3300 | 3 | 3300 | 0 | 0 | 3 | 3300 | 0
56 | Supply of Fittings for washout of water tanks ,3" Dia MS. Flange | set | 6 | 700 | 4200 | 6 | 4200 | 0 | 0 | 6 | 4200 | 0
57 | Supply of Fittings for washout of water tanks ,3" Dia G.I. Plug . | pc | 3 | 400 | 1200 | 3 | 1200 | 0 | 0 | 3 | 1200 | 0
58 | Supply of Fittings for washout of water tanks ,3" Dia G.I./HDPE Flange Set. | set | 3 | 1850 | 5550 | 3 | 5550 | 0 | 0 | 3 | 5550 | 0
59 | Providing and fixing of Barbed wire fencing all complete | rm | 1724.58 | 1000 | 1724580 | 1782.96 | 1782960 | 0 | 0 | 1782.96 | 1782960 | 58.38
60 | providing 6 mm ø mild steel rod for hooks, 650 mm long each for fencing works | kg | 35.4 | 150 | 5310 | 0 | 0 | 0 | 0 | 0 | 0 | -35.4
61 | providing M.S. 40 x 40 x 6 angle bar, 2.5 m long for fencing all complete | kg | 1077.99 | 150 | 161698.5 | 560 | 84000 | 0 | 0 | 560 | 84000 | -517.99
62 | Providing and laying granular sub-base without compaction on prepared surface, mixing , complete as per Drawing and Technical Specifications., By Mechanical means | m3 | 135 | 2500 | 337500 | 0 | 0 | 0 | 0 | 0 | 0 | -135
63 | Earthwork Excavation in Cutting., Roadway Excavation in all types of Soil by Mechanical Means ., Road way Excavation in all types of soil as per Drawing and technical specifications including removal of stumps and other deleterious matter, all lifts and lead as per Drawing and instruction of the Engineer as required on site for Access road required for the proposed Structures | m3 | 600 | 50 | 30000 | 440 | 22000 | 0 | 0 | 440 | 22000 | -160
| Total |  |  |  | 11340909 |  | 5842510.5533 |  | 4893782.2308 |  | 10736292.7841 | 0
| 13 % VAT |  |  |  | 1474318.17 |  | 759526.3719 |  | 636191.69 |  | 1395718.0619 | 0
|  | Total with VAT |  |  | 12815227.17 |  | 6602036.9252 |  | 5529973.9208 |  | 12132010.846 | 0
Provisional sum
| Project information Board with metal frame on site | ps | 3 | 5000 | 15000 | 0 | 0 | 2 | 10000 | 2 | 10000 | -1
| Lab test for concrete as instructed by site engineer | ps | 1 | 45000 | 45000 | 1 | 22400 | 1 | 22600 | 1 | 45000 | 0
| Insurance | ps | 1 | 30000 | 30000 | 0 | 0 | 1 | 30000 | 1 | 30000 | 0
| Supply of required fittings and required materials and extra works on site as per the approval of Engineer | ps | 1 | 300000 | 300000 | 1 | 199619.02 | 1 | 35494 | 1 | 235113.02 | 0
0
| Grand total Rs. |  |  |  | 13205227.17 |  | 6824055.9452 |  | 5628067.9208 |  | 12452123.866 | 0 | 42.62
उपर्युक्त बमोजिम ठीक छ भनी प्रमाणित गर्नेको सही ः–
| यो बमोजिमको जम्मा रु. |  | 12452123.866 |  |  |  |  | भ्याट सहित | ङ) धरौटी @5% का दरले |  | 292125.5277
| अघिल्लो बिलबाट भुक्तानी भएको रु. |  | 5628067.9208 |  |  |  |  | भ्याट सहित | च) अग्रीम आयकरः – 1.5% का दरले जम्मा रु.
| बाँकी दिनु पर्ने रु. |  | 6824055.9452 |  |  |  |  | भ्याट सहित | ठेकेदारको सही ः–
| कट्टा गर्नू पर्ने रु | [7 empty] | खुद दिनु पर्ने रु.
| क) पेश्की | [7 empty] | जम्मा रु: …………………..……...अक्षेरेपी...............को चेक नं
| नाप जाँच गर्नेको सही |  |  | चेक गर्नेको सही | [6 empty] | स्वीकृत गर्नेको सही